0.6/1kV XLPE Insulated Power Cables

APPLICATION

The products are used for electrical power transmission and distribution systems, operating at A.C. rated voltage of(U0/U) 0.6/1kV and below.These cables are suitable for electricity supply in low voltage distribution power networks,industrial installations, in buildings and operation stations .These cables can be fixed on cable trays, indoors, in cable ducts, outdoors and underground .

STANDARDS

IEC 60228 Conductors of insulated cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from

1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV(Um=1.2kV) and

3 kV(Um=3.6kV)

Note: We also can produce based on other international standards, such as BS , AS/NZS, VDE and other standards.

CHAIRCTERITICS

● Maximum conductor temperature in normal operation: 90˚C.

● Short Circuit Temperature ( 5 seconds maximum duration ): Shall not exceed 250˚C.

●Good electrical and mechanical properties.

● Minimum bending radius:

| Items | Single-core Cables |  | Three-core Cables |  |
| --- | --- | --- | --- | --- |
|  | Unarmoured | Armoured | Unarmoured | Armoured |
| Min. bending radius during installation | 20D | 15D | 15D | 12D |
| Min. bending radius close to connection box and termination (bending radius should be controlled carefully, if the molding guide plate is used) | 15D | 12D | 12D | 10D |

Note:D is overall diameter of cable.

TYPE & SPECIFICATION

| Type |  | Designation |
| --- | --- | --- |
| N2XY(YJV) | NA2XY(YJLV) | Cu or Al Core XLPE Insulated PVC Sheathed Power Cable |
| N2X2Y(YJY) | NA2X2Y(YJLY) | Cu or Al Core XLPE Insulated PE Sheathed Power Cable |
| N2XBY(YJV62) | NA2XBY(YJLV62) | Cu or Al Core XLPE Insulated Non-Magnetic Metal Tape Armoured PVC Sheathed Power Cable |
| N2XB2Y(YJY63) | NA2XB2Y(YJLY63) | Cu or Al Core XLPE Insulated Non-Magnetic Metal Tape Armoured PE Sheathed Power Cable |
| N2XRY(YJV72) | NA2XRY (YJLV72) | Cu or Al Core XLPE Insulated Non-Magnetic Wire Armoured PVC Sheathed Power Cable |
| N2XR2Y(YJY73 ) | NA2XR2Y(YJLY73 ) | Cu or Al Core XLPE Insulated Non-Magnetic Wire Armoured PE Sheathed Power Cable |
| N2XBY(YJV22 ) | NA2XBY(YJLV22) | Cu or Al Core XLPE Insulated Steel Tape Armoured PVC Sheathed Power Cable |
| N2XB2Y(YJY23) | NA2XB2Y(YJLY23) | Cu or Al Core XLPE Insulated Steel Tape Armoured PE Sheathed Power Cable |
| N2XRY(YJV32) | NA2XRY(YJLV32) | Cu or Al Core XLPE Insulated Steel Wire Armoured PVC Sheathed Power Cable |
| N2XR2Y(YJY33) | NA2XR2Y(YJLY33) | Cu or Al Core XLPE Insulated Steel Wire Armoured PE Sheathed Power Cable |

CONSTRUCTION STRUCTION

Conductors

The conductors shall be either of Class 1 or Class 2 of plain or metal-coated annealed copper or of plain aluminium or aluminium alloy, or of Class 5 of plain or metal-coated copper in accordance with IEC 60228.

Insulation

This will be an extruded layer of XLPE applied over conductor

Laying-up

In case of multi-core cables, the multi-core are laid up with non-hygroscopic fillers at interstices and a binder tape is applied with an overlap. These binder tapes can be of or non-hygroscopic material.

Inner sheath

Extruded layer of PVC or PE is applied over the laid up cores for armoured cables. PVC is normally of grade ST1 and PE of grade ST3 as per IEC 60502 -1.

Armour

Armour shall be as per IEC 60502-1 of the following types:

- Round Wire Armour

- Double Tape Armour

Armour material shall be Galvanized steel for three core cables and Non-magnetic material (Non-magnetic steel or Aluminium etc.) for single core cables. Armour of other material as per IEC 60502-1 can be provided upon request.

Outer Sheath

Outer sheath material can be either PVC, LDPE, MDPE, HDPE or LSZH.Other colors may be provided to suit a range of installation considerations such as the effect of UV radiations.When the cable is required to ant-termite / anti-vermin, a special additive is added to the sheathing compound.

Flame-retardant (optional)

In the event of a fire, there is a risk of the fire spreading through cables. To prevent this from happening, cables can be provided with sheaths made of a flame retardant material.

YJV(N2XY)  Single Core  0.6/1kV

CU/XLPE/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2, solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 1×1.5 | 1 | 0.7 | 1.4 | 5.6 | 44 | 12.1 |
| 1×2.5 | 1 | 0.7 | 1.4 | 6.0 | 55 | 7.41 |
| 1×4 | 1 | 0.7 | 1.4 | 6.4 | 72 | 4.61 |
| 1×6 | 1 | 0.7 | 1.4 | 6.9 | 95 | 3.08 |
| 1×10 | 6 | 0.7 | 1.4 | 8.2 | 140 | 1.83 |
| 1×16 | 6 | 0.7 | 1.4 | 9.0 | 199 | 1.15 |
| 1×25 | 6 | 0.9 | 1.4 | 10.6 | 295 | 0.727 |
| 1×35 | 6 | 0.9 | 1.4 | 11.6 | 389 | 0.524 |
| 1×50 | 6 | 1.0 | 1.4 | 13.1 | 512 | 0.387 |
| 1×70 | 12 | 1.1 | 1.4 | 14.8 | 714 | 0.268 |
| 1×95 | 15 | 1.1 | 1.5 | 16.8 | 968 | 0.193 |
| 1×120 | 18 | 1.2 | 1.5 | 18.4 | 1204 | 0.153 |
| 1×150 | 18 | 1.4 | 1.6 | 20.5 | 1484 | 0.124 |
| 1×185 | 30 | 1.6 | 1.6 | 22.5 | 1847 | 0.0991 |
| 1×240 | 34 | 1.7 | 1.7 | 25.2 | 2385 | 0.0754 |
| 1×300 | 34 | 1.8 | 1.8 | 27.8 | 2970 | 0.0601 |
| 1×400 | 53 | 2.0 | 1.9 | 31.2 | 3803 | 0.0470 |
| 1×500 | 53 | 2.2 | 2.0 | 34.7 | 4801 | 0.0366 |
| 1×630 | 53 | 2.4 | 2.2 | 39.2 | 6196 | 0.0283 |

YJV(N2XY)  Multi- Core  0.6/1kV

CU/XLPE/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler: Non-hygroscopic material

- Binder: Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.7 | 1.8 | 9.4 | 105 | 12.1 |
| 2×2.5 | 1 | 0.7 | 1.8 | 10.2 | 132 | 7.41 |
| 2×4 | 1 | 0.7 | 1.8 | 11.2 | 172 | 4.61 |
| 2×6 | 1 | 0.7 | 1.8 | 12.2 | 222 | 3.08 |
| 2×10 | 6 | 0.7 | 1.8 | 14.7 | 330 | 1.83 |
| 2×16 | 6 | 0.7 | 1.8 | 16.3 | 461 | 1.15 |
| 2×25 | 6 | 0.9 | 1.8 | 19.5 | 679 | 0.727 |
| 2×35 | 6 | 0.9 | 1.8 | 21.5 | 886 | 0.524 |
| 2×50 | 6 | 1.0 | 1.8 | 24.5 | 1166 | 0.387 |
| 2×70 | 12 | 1.1 | 1.8 | 27.9 | 1587 | 0.268 |
| 2×95 | 15 | 1.1 | 2.0 | 32.2 | 2161 | 0.193 |
| 2×120 | 18 | 1.2 | 2.1 | 35.6 | 2694 | 0.153 |
| 2×150 | 18 | 1.4 | 2.2 | 39.6 | 3312 | 0.124 |
| 2×185 | 30 | 1.6 | 2.3 | 43.8 | 4127 | 0.0991 |
| 2×240 | 34 | 1.7 | 2.5 | 49.2 | 5322 | 0.0754 |
| 2×300 | 34 | 1.8 | 2.7 | 54.4 | 6622 | 0.0601 |
| 2×400 | 53 | 2.0 | 2.9 | 61.2 | 8470 | 0.0470 |
| 3×1.5 | 1 | 0.7 | 1.8 | 9.9 | 126 | 12.1 |
| 3×2.5 | 1 | 0.7 | 1.8 | 10.7 | 161 | 7.41 |
| 3×4 | 1 | 0.7 | 1.8 | 11.7 | 216 | 4.61 |
| 3×6 | 1 | 0.7 | 1.8 | 12.8 | 285 | 3.08 |
| 3×10 | 6 | 0.7 | 1.8 | 15.6 | 432 | 1.83 |
| 3×16 | 6 | 0.7 | 1.8 | 17.3 | 617 | 1.15 |
| 3×25 | 6 | 0.9 | 1.8 | 20.7 | 918 | 0.727 |
| 3X35 | 6 | 0.9 | 1.8 | 22.9 | 1213 | 0.524 |
| 3×50 | 6 | 1.0 | 1.8 | 26.1 | 1605 | 0.387 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×70 | 12 | 1.1 | 1.9 | 30.3 | 2240 | 0.268 |
| 3×95 | 15 | 1.1 | 2.0 | 34.4 | 3028 | 0.193 |
| 3×120 | 18 | 1.2 | 2.1 | 38.1 | 3786 | 0.153 |
| 3×150 | 18 | 1.4 | 2.3 | 42.6 | 4679 | 0.124 |
| 3×185 | 30 | 1.6 | 2.4 | 47.1 | 5842 | 0.0991 |
| 3×240 | 34 | 1.7 | 2.6 | 52.9 | 7547 | 0.0754 |
| 3×300 | 34 | 1.8 | 2.8 | 58.5 | 9400 | 0.0601 |
| 3×400 | 53 | 2.0 | 3.1 | 66.0 | 12068 | 0.0470 |
| 4×1.5 | 1 | 0.7 | 1.8 | 10.6 | 150 | 12.1 |
| 4×2.5 | 1 | 0.7 | 1.8 | 11.5 | 196 | 7.41 |
| 4×4 | 1 | 0.7 | 1.8 | 12.7 | 266 | 4.61 |
| 4×6 | 1 | 0.7 | 1.8 | 13.9 | 356 | 3.08 |
| 4×10 | 6 | 0.7 | 1.8 | 17.0 | 545 | 1.83 |
| 4×16 | 6 | 0.7 | 1.8 | 18.9 | 787 | 1.15 |
| 4×25 | 6 | 0.9 | 1.8 | 22.8 | 1179 | 0.727 |
| 4×35 | 6 | 0.9 | 1.8 | 25.2 | 1565 | 0.524 |
| 4×50 | 6 | 1.0 | 1.9 | 29.0 | 2090 | 0.387 |
| 4×70 | 12 | 1.1 | 2.0 | 33.6 | 2926 | 0.268 |
| 4×95 | 15 | 1.1 | 2.1 | 38.2 | 3962 | 0.193 |
| 4×120 | 18 | 1.2 | 2.3 | 42.5 | 4976 | 0.153 |
| 4×150 | 18 | 1.4 | 2.4 | 47.3 | 6125 | 0.124 |
| 4×185 | 30 | 1.6 | 2.6 | 52.5 | 7677 | 0.0991 |
| 4×240 | 34 | 1.7 | 2.8 | 59.0 | 9918 | 0.0754 |
| 4×300 | 34 | 1.8 | 3.0 | 65.2 | 12355 | 0.0601 |
| 4×400 | 53 | 2.0 | 3.3 | 73.5 | 15859 | 0.0470 |
| 5×1.5 | 1 | 0.7 | 1.8 | 11.4 | 176 | 12.1 |
| 5×2.5 | 1 | 0.7 | 1.8 | 12.4 | 232 | 7.41 |
| 5×4 | 1 | 0.7 | 1.8 | 13.7 | 318 | 4.61 |
| 5×6 | 1 | 0.7 | 1.8 | 15.1 | 430 | 3.08 |
| 5×10 | 6 | 0.7 | 1.8 | 18.5 | 662 | 1.83 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 5×16 | 6 | 0.7 | 1.8 | 20.6 | 962 | 1.15 |
| 5×25 | 6 | 0.9 | 1.8 | 25.0 | 1448 | 0.727 |
| 5×35 | 6 | 0.9 | 1.8 | 27.7 | 1928 | 0.524 |
| 5×50 | 6 | 1.0 | 2.0 | 32.4 | 2600 | 0.387 |
| 5×70 | 12 | 1.1 | 2.1 | 37.2 | 3630 | 0.268 |
| 5×95 | 15 | 1.1 | 2.3 | 42.5 | 4938 | 0.193 |
| 5×120 | 18 | 1.2 | 2.4 | 47.0 | 6177 | 0.153 |
| 5×150 | 18 | 1.4 | 2.6 | 52.5 | 7629 | 0.124 |
| 5×185 | 30 | 1.6 | 2.8 | 58.3 | 9559 | 0.0991 |
| 5×240 | 34 | 1.7 | 3.0 | 65.5 | 12348 | 0.0754 |
| 5×300 | 34 | 1.8 | 3.2 | 72.3 | 15381 | 0.0601 |
| 5×400 | 53 | 2.0 | 3.6 | 81.8 | 19775 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.7/0.7 | 1.8 | 11.3 | 184 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 1.8 | 12.4 | 248 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 1.8 | 13.6 | 334 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 1.8 | 16.2 | 497 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 1.8 | 18.4 | 726 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 1.8 | 21.8 | 1079 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 1.8 | 23.6 | 1366 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 1.8 | 27.3 | 1849 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 1.9 | 31.5 | 2572 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 2.1 | 36.1 | 3494 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.2/1.1 | 2.2 | 40.2 | 4452 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.4/1.1 | 2.3 | 43.9 | 5309 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 49.0 | 6736 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 1.7/1.2 | 2.7 | 54.9 | 8666 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 1.8/1.4 | 2.9 | 60.8 | 10783 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 3.1 | 68.2 | 13768 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.7/0.7 | 1.8 | 12.0 | 210 | 7.41/12.1 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 1.8 | 13.2 | 284 | 4.61/7.41 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 1.8 | 14.5 | 385 | 3.08/4.61 |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 1.8 | 17.1 | 568 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 1.8 | 19.8 | 841 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 1.8 | 23.2 | 1250 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 1.8 | 24.9 | 1535 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 1.9 | 29.5 | 2133 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 2.0 | 35.2 | 3198 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 2.2 | 38.5 | 3987 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.2/1.1 | 2.3 | 43.1 | 5152 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.4/1.1 | 2.4 | 46.4 | 6003 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 2.6 | 52.0 | 7683 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 1.7/1.2 | 2.8 | 58.1 | 9853 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 1.8/1.4 | 3.0 | 64.5 | 12249 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 3.2 | 72.2 | 15602 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.7/0.7 | 1.8 | 12.2 | 221 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 1.8 | 13.4 | 301 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 1.8 | 14.8 | 407 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 1.8 | 17.8 | 615 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 1.8 | 20.2 | 902 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 1.8 | 24.1 | 1349 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 1.8 | 26.3 | 1730 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 1.9 | 30.9 | 2359 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 2.1 | 35.5 | 3291 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 2.2 | 40.4 | 4452 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.2/1.1 | 2.4 | 45.1 | 5673 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.4/1.1 | 2.5 | 49.4 | 6812 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 2.7 | 55.1 | 8617 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 1.7/1.2 | 2.9 | 61.8 | 11095 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 1.8/1.4 | 3.1 | 68.4 | 13808 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 3.4 | 77.0 | 17677 | 0.0470/0.0991 |

YJLV (NA2XY)  Single Core  0.6/1kV

AL/XLPE/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 1×2.5 | 1 | 0.7 | 1.4 | 6.0 | 41 | 12.1 |
| 1×4 | 1 | 0.7 | 1.4 | 6.4 | 49 | 7.41 |
| 1×6 | 1 | 0.7 | 1.4 | 6.9 | 59 | 4.61 |
| 1×10 | 6 | 0.7 | 1.4 | 8.2 | 77 | 3.08 |
| 1×16 | 6 | 0.7 | 1.4 | 9.0 | 101 | 1.91 |
| 1×25 | 6 | 0.9 | 1.4 | 10.6 | 143 | 1.20 |
| 1×35 | 6 | 0.9 | 1.4 | 11.6 | 177 | 0.868 |
| 1×50 | 6 | 1.0 | 1.4 | 13.1 | 224 | 0.641 |
| 1×70 | 12 | 1.1 | 1.4 | 14.8 | 300 | 0.443 |
| 1×95 | 15 | 1.1 | 1.5 | 16.8 | 394 | 0.320 |
| 1×120 | 15 | 1.2 | 1.5 | 18.4 | 476 | 0.253 |
| 1×150 | 15 | 1.4 | 1.6 | 20.5 | 587 | 0.206 |
| 1×185 | 30 | 1.6 | 1.6 | 22.5 | 717 | 0.164 |
| 1×240 | 30 | 1.7 | 1.7 | 25.2 | 918 | 0.125 |
| 1×300 | 30 | 1.8 | 1.8 | 27.8 | 1130 | 0.100 |
| 1×400 | 53 | 2.0 | 1.9 | 31.2 | 1431 | 0.0778 |
| 1×500 | 53 | 2.2 | 2.0 | 34.7 | 1794 | 0.0605 |
| 1×630 | 53 | 2.4 | 2.2 | 39.2 | 2292 | 0.0469 |

YJLV (NA2XY)  Multi- Core  0.6/1kV

AL/XLPE/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler: Non-hygroscopic material

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.7 | 1.8 | 10.2 | 103 | 12.1 |
| 2×4 | 1 | 0.7 | 1.8 | 11.2 | 124 | 7.41 |
| 2×6 | 1 | 0.7 | 1.8 | 12.2 | 150 | 4.61 |
| 2×10 | 6 | 0.7 | 1.8 | 14.7 | 199 | 3.08 |
| 2×16 | 6 | 0.7 | 1.8 | 16.3 | 263 | 1.91 |
| 2×25 | 6 | 0.9 | 1.8 | 19.5 | 372 | 1.20 |
| 2×35 | 6 | 0.9 | 1.8 | 21.5 | 461 | 0.868 |
| 2×50 | 6 | 1.0 | 1.8 | 24.5 | 582 | 0.641 |
| 2×70 | 12 | 1.1 | 1.8 | 27.9 | 754 | 0.443 |
| 2×95 | 15 | 1.1 | 2.0 | 32.2 | 1007 | 0.320 |
| 2×120 | 15 | 1.2 | 2.1 | 35.6 | 1224 | 0.253 |
| 2×150 | 15 | 1.4 | 2.2 | 39.6 | 1508 | 0.206 |
| 2×185 | 30 | 1.6 | 2.3 | 43.8 | 1855 | 0.164 |
| 2×240 | 30 | 1.7 | 2.5 | 49.2 | 2374 | 0.125 |
| 2×300 | 30 | 1.8 | 2.7 | 54.4 | 2919 | 0.100 |
| 2×400 | 53 | 2.0 | 2.9 | 61.2 | 3692 | 0.0778 |
| 3×2.5 | 1 | 0.7 | 1.8 | 10.7 | 118 | 12.1 |
| 3×4 | 1 | 0.7 | 1.8 | 11.7 | 144 | 7.41 |
| 3×6 | 1 | 0.7 | 1.8 | 12.8 | 177 | 4.61 |
| 3×10 | 6 | 0.7 | 1.8 | 15.6 | 238 | 3.08 |
| 3×16 | 6 | 0.7 | 1.8 | 17.3 | 319 | 1.91 |
| 3×25 | 6 | 0.9 | 1.8 | 20.7 | 459 | 1.20 |
| 3X35 | 6 | 0.9 | 1.8 | 22.9 | 575 | 0.868 |
| 3×50 | 6 | 1.0 | 1.8 | 26.1 | 733 | 0.641 |
| 3×70 | 12 | 1.1 | 1.9 | 30.3 | 992 | 0.443 |
| 3×95 | 15 | 1.1 | 2.0 | 34.4 | 1297 | 0.320 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×120 | 15 | 1.2 | 2.1 | 38.1 | 1586 | 0.253 |
| 3×150 | 15 | 1.4 | 2.3 | 42.6 | 1973 | 0.206 |
| 3×185 | 30 | 1.6 | 2.4 | 47.1 | 2434 | 0.164 |
| 3×240 | 30 | 1.7 | 2.6 | 52.9 | 3123 | 0.125 |
| 3×300 | 30 | 1.8 | 2.8 | 58.5 | 3849 | 0.100 |
| 3×400 | 53 | 2.0 | 3.1 | 66.0 | 4908 | 0.0778 |
| 4×2.5 | 1 | 0.7 | 1.8 | 11.5 | 137 | 12.1 |
| 4×4 | 1 | 0.7 | 1.8 | 12.7 | 170 | 7.41 |
| 4×6 | 1 | 0.7 | 1.8 | 13.9 | 211 | 4.61 |
| 4×10 | 6 | 0.7 | 1.8 | 17.0 | 287 | 3.08 |
| 4×16 | 6 | 0.7 | 1.8 | 18.9 | 390 | 1.91 |
| 4×25 | 6 | 0.9 | 1.8 | 22.8 | 567 | 1.20 |
| 4×35 | 6 | 0.9 | 1.8 | 25.2 | 715 | 0.868 |
| 4×50 | 6 | 1.0 | 1.9 | 29.0 | 929 | 0.641 |
| 4×70 | 12 | 1.1 | 2.0 | 33.6 | 1262 | 0.443 |
| 4×95 | 15 | 1.1 | 2.1 | 38.2 | 1654 | 0.320 |
| 4×120 | 15 | 1.2 | 2.3 | 42.5 | 2044 | 0.253 |
| 4×150 | 15 | 1.4 | 2.4 | 47.3 | 2517 | 0.206 |
| 4×185 | 30 | 1.6 | 2.6 | 52.5 | 3133 | 0.164 |
| 4×240 | 30 | 1.7 | 2.8 | 59.0 | 4021 | 0.125 |
| 4×300 | 30 | 1.8 | 3.0 | 65.2 | 4955 | 0.100 |
| 4×400 | 53 | 2.0 | 3.3 | 73.5 | 6316 | 0.0778 |
| 5×2.5 | 1 | 0.7 | 1.8 | 12.4 | 159 | 12.1 |
| 5×4 | 1 | 0.7 | 1.8 | 13.7 | 198 | 7.41 |
| 5×6 | 1 | 0.7 | 1.8 | 15.1 | 249 | 4.61 |
| 5×10 | 6 | 0.7 | 1.8 | 18.5 | 340 | 3.08 |
| 5×16 | 6 | 0.7 | 1.8 | 20.6 | 466 | 1.91 |
| 5×25 | 6 | 0.9 | 1.8 | 25.0 | 682 | 1.20 |
| 5×35 | 6 | 0.9 | 1.8 | 27.7 | 865 | 0.868 |
| 5×50 | 6 | 1.0 | 2.0 | 32.4 | 1149 | 0.641 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 5×70 | 12 | 1.1 | 2.1 | 37.2 | 1550 | 0.443 |
| 5×95 | 15 | 1.1 | 2.3 | 42.5 | 2053 | 0.320 |
| 5×120 | 15 | 1.2 | 2.4 | 47.0 | 2513 | 0.253 |
| 5×150 | 15 | 1.4 | 2.6 | 52.5 | 3119 | 0.206 |
| 5×185 | 30 | 1.6 | 2.8 | 58.3 | 3879 | 0.164 |
| 5×240 | 30 | 1.7 | 3.0 | 65.5 | 4976 | 0.125 |
| 5×300 | 30 | 1.8 | 3.2 | 72.3 | 6131 | 0.100 |
| 5×400 | 53 | 2.0 | 3.6 | 81.8 | 7846 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 1.8 | 12.4 | 162 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 1.8 | 13.6 | 201 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 1.8 | 16.2 | 268 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 1.8 | 18.4 | 364 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 1.8 | 21.8 | 521 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 1.8 | 23.6 | 630 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 1.8 | 27.3 | 826 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 1.9 | 31.5 | 1111 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 2.1 | 36.1 | 1472 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.2/1.1 | 2.2 | 40.2 | 1838 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.4/1.1 | 2.3 | 43.9 | 2188 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 49.0 | 2751 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 1.7/1.2 | 2.7 | 54.9 | 3508 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 1.8/1.4 | 2.9 | 60.8 | 4332 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 3.1 | 68.2 | 5476 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 1.8 | 13.2 | 182 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 1.8 | 14.5 | 228 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 1.8 | 17.1 | 303 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 1.8 | 19.8 | 415 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 1.8 | 23.2 | 593 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 1.8 | 24.9 | 700 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 1.9 | 29.5 | 949 | 0.641/1.20 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 2.0 | 35.2 | 1266 | 0.443/0.868 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 2.2 | 38.5 | 1674 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.2/1.1 | 2.3 | 43.1 | 2122 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.4/1.1 | 2.4 | 46.4 | 2466 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 2.6 | 52.0 | 3121 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 1.7/1.2 | 2.8 | 58.1 | 3962 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 1.8/1.4 | 3.0 | 64.5 | 4896 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 3.2 | 72.2 | 6175 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 1.8 | 13.4 | 190 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 1.8 | 14.8 | 238 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 1.8 | 17.8 | 322 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 1.8 | 20.2 | 441 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 1.8 | 24.1 | 638 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 1.8 | 26.3 | 782 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 1.9 | 30.9 | 1045 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 2.1 | 35.5 | 1414 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 2.2 | 40.4 | 1853 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.2/1.1 | 2.4 | 45.1 | 2326 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.4/1.1 | 2.5 | 49.4 | 2788 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 2.7 | 55.1 | 3495 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 1.7/1.2 | 2.9 | 61.8 | 4463 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 1.8/1.4 | 3.1 | 68.4 | 5507 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 3.4 | 77.0 | 7000 | 0.0778/0.164 |

YJV62 (N2XBY)  Single Core  0.6/1kV

CU/XLPE/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Inner covering: Polyvinyl chloride PVC

- Armour: Non-magnetic steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magnetic steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 0.7 | 0.2 | 1.4 | 11.0 | 245 | 1.83 |
| 1×16 | 6 | 0.7 | 0.2 | 1.4 | 11.8 | 314 | 1.15 |
| 1×25 | 6 | 0.9 | 0.2 | 1.4 | 13.4 | 429 | 0.727 |
| 1×35 | 6 | 0.9 | 0.2 | 1.4 | 14.4 | 535 | 0.524 |
| 1×50 | 6 | 1.0 | 0.2 | 1.4 | 15.9 | 676 | 0.387 |
| 1×70 | 12 | 1.1 | 0.2 | 1.5 | 17.8 | 906 | 0.268 |
| 1×95 | 15 | 1.1 | 0.2 | 1.6 | 19.8 | 1184 | 0.193 |
| 1×120 | 18 | 1.2 | 0.2 | 1.6 | 21.4 | 1441 | 0.153 |
| 1×150 | 18 | 1.4 | 0.2 | 1.7 | 23.5 | 1745 | 0.124 |
| 1×185 | 30 | 1.6 | 0.2 | 1.7 | 25.5 | 2134 | 0.0991 |
| 1×240 | 34 | 1.7 | 0.2 | 1.8 | 28.2 | 2704 | 0.0754 |
| 1×300 | 34 | 1.8 | 0.2 | 1.9 | 30.8 | 3321 | 0.0601 |
| 1×400 | 53 | 2.0 | 0.2 | 2.0 | 34.6 | 4232 | 0.0470 |
| 1×500 | 53 | 2.2 | 0.5 | 2.2 | 39.5 | 5664 | 0.0366 |
| 1×630 | 53 | 2.4 | 0.5 | 2.3 | 43.8 | 7143 | 0.0283 |

YJLV62 (NA2XBY)  Single Core  0.6/1kV

AL/XLPE/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Inner sheath : Polyvinyl chloride PVC

- Armour: Non-magnetic steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magnetic steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 0.7 | 0.2 | 1.4 | 11.0 | 179 | 3.08 |
| 1×16 | 6 | 0.7 | 0.2 | 1.4 | 11.8 | 215 | 1.91 |
| 1×25 | 6 | 0.9 | 0.2 | 1.4 | 13.4 | 276 | 1.20 |
| 1×35 | 6 | 0.9 | 0.2 | 1.4 | 14.4 | 323 | 0.868 |
| 1×50 | 6 | 1.0 | 0.2 | 1.4 | 15.9 | 385 | 0.641 |
| 1×70 | 12 | 1.1 | 0.2 | 1.5 | 17.8 | 492 | 0.443 |
| 1×95 | 15 | 1.1 | 0.2 | 1.6 | 19.8 | 610 | 0.320 |
| 1×120 | 15 | 1.2 | 0.2 | 1.6 | 21.4 | 710 | 0.253 |
| 1×150 | 15 | 1.4 | 0.2 | 1.7 | 23.5 | 848 | 0.206 |
| 1×185 | 30 | 1.6 | 0.2 | 1.7 | 25.5 | 1003 | 0.164 |
| 1×240 | 30 | 1.7 | 0.2 | 1.8 | 28.2 | 1237 | 0.125 |
| 1×300 | 30 | 1.8 | 0.2 | 1.9 | 30.8 | 1480 | 0.100 |
| 1×400 | 53 | 2.0 | 0.2 | 2.0 | 34.6 | 1857 | 0.0778 |
| 1×500 | 53 | 2.2 | 0.5 | 2.2 | 39.5 | 2657 | 0.0605 |
| 1×630 | 53 | 2.4 | 0.5 | 2.3 | 43.8 | 3239 | 0.0469 |

YJV22 (N2XBY)  Multi-Core  0.6/1kV

CU/XLPE/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Copper,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler: Non-hygroscopic material

- Binder: Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.7 | 0.2 | 1.8 | 12.2 | 220 | 12.1 |
| 2×2.5 | 1 | 0.7 | 0.2 | 1.8 | 13.0 | 256 | 7.41 |
| 2×4 | 1 | 0.7 | 0.2 | 1.8 | 14.0 | 307 | 4.61 |
| 2×6 | 1 | 0.7 | 0.2 | 1.8 | 15.0 | 370 | 3.08 |
| 2×10 | 6 | 0.7 | 0.2 | 1.8 | 17.5 | 509 | 1.83 |
| 2×16 | 6 | 0.7 | 0.2 | 1.8 | 19.1 | 659 | 1.15 |
| 2×25 | 6 | 0.9 | 0.2 | 1.8 | 22.3 | 915 | 0.727 |
| 2×35 | 6 | 0.9 | 0.2 | 1.8 | 24.3 | 1147 | 0.524 |
| 2×50 | 6 | 1.0 | 0.2 | 1.8 | 27.3 | 1463 | 0.387 |
| 2×70 | 12 | 1.1 | 0.2 | 1.9 | 30.9 | 1939 | 0.268 |
| 2×95 | 15 | 1.1 | 0.2 | 2.0 | 35.4 | 2587 | 0.193 |
| 2×120 | 18 | 1.2 | 0.5 | 2.2 | 40.2 | 3557 | 0.153 |
| 2×150 | 18 | 1.4 | 0.5 | 2.3 | 44.2 | 4269 | 0.124 |
| 2×185 | 30 | 1.6 | 0.5 | 2.5 | 49.0 | 5250 | 0.0991 |
| 2×240 | 34 | 1.7 | 0.5 | 2.6 | 54.2 | 6551 | 0.0754 |
| 2×300 | 34 | 1.8 | 0.5 | 2.8 | 59.8 | 8038 | 0.0601 |
| 2×400 | 53 | 2.0 | 0.5 | 3.0 | 66.6 | 10056 | 0.0470 |
| 3×1.5 | 1 | 0.7 | 0.2 | 1.8 | 12.7 | 246 | 12.1 |
| 3×2.5 | 1 | 0.7 | 0.2 | 1.8 | 13.5 | 292 | 7.41 |
| 3×4 | 1 | 0.7 | 0.2 | 1.8 | 14.5 | 359 | 4.61 |
| 3×6 | 1 | 0.7 | 0.2 | 1.8 | 15.6 | 441 | 3.08 |
| 3×10 | 6 | 0.7 | 0.2 | 1.8 | 18.4 | 621 | 1.83 |
| 3×16 | 6 | 0.7 | 0.2 | 1.8 | 20.1 | 827 | 1.15 |
| 3×25 | 6 | 0.9 | 0.2 | 1.8 | 23.5 | 1170 | 0.727 |
| 3X35 | 6 | 0.9 | 0.2 | 1.8 | 25.7 | 1491 | 0.524 |
| 3×50 | 6 | 1.0 | 0.2 | 1.8 | 28.9 | 1922 | 0.387 |
| 3×70 | 12 | 1.1 | 0.2 | 2.0 | 33.7 | 2657 | 0.268 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×95 | 15 | 1.1 | 0.5 | 2.2 | 39.2 | 3884 | 0.193 |
| 3×120 | 18 | 1.2 | 0.5 | 2.3 | 42.9 | 4728 | 0.153 |
| 3×150 | 18 | 1.4 | 0.5 | 2.4 | 47.6 | 5749 | 0.124 |
| 3×185 | 30 | 1.6 | 0.5 | 2.6 | 52.3 | 7045 | 0.0991 |
| 3×240 | 34 | 1.7 | 0.5 | 2.7 | 58.3 | 8927 | 0.0754 |
| 3×300 | 34 | 1.8 | 0.5 | 2.9 | 63.9 | 10919 | 0.0601 |
| 3×400 | 53 | 2.0 | 0.5 | 3.2 | 71.4 | 13772 | 0.0470 |
| 4×1.5 | 1 | 0.7 | 0.2 | 1.8 | 13.4 | 279 | 12.1 |
| 4×2.5 | 1 | 0.7 | 0.2 | 1.8 | 14.3 | 336 | 7.41 |
| 4×4 | 1 | 0.7 | 0.2 | 1.8 | 15.5 | 420 | 4.61 |
| 4×6 | 1 | 0.7 | 0.2 | 1.8 | 16.7 | 525 | 3.08 |
| 4×10 | 6 | 0.7 | 0.2 | 1.8 | 19.8 | 751 | 1.83 |
| 4×16 | 6 | 0.7 | 0.2 | 1.8 | 21.7 | 1016 | 1.15 |
| 4×25 | 6 | 0.9 | 0.2 | 1.8 | 25.6 | 1455 | 0.727 |
| 4×35 | 6 | 0.9 | 0.2 | 1.8 | 28.0 | 1871 | 0.524 |
| 4×50 | 6 | 1.0 | 0.2 | 1.9 | 31.8 | 2440 | 0.387 |
| 4×70 | 12 | 1.1 | 0.2 | 2.1 | 37.0 | 3387 | 0.268 |
| 4×95 | 15 | 1.1 | 0.5 | 2.3 | 43.0 | 4907 | 0.193 |
| 4×120 | 18 | 1.2 | 0.5 | 2.4 | 47.5 | 6044 | 0.153 |
| 4×150 | 18 | 1.4 | 0.5 | 2.6 | 52.5 | 7332 | 0.124 |
| 4×185 | 30 | 1.6 | 0.5 | 2.7 | 57.9 | 9048 | 0.0991 |
| 4×240 | 34 | 1.7 | 0.5 | 2.9 | 64.4 | 11449 | 0.0754 |
| 4×300 | 34 | 1.8 | 0.5 | 3.1 | 70.6 | 14041 | 0.0601 |
| 4×400 | 53 | 2.0 | 0.5 | 3.4 | 79.3 | 17835 | 0.0470 |
| 5×1.5 | 1 | 0.7 | 0.2 | 1.8 | 14.2 | 314 | 12.1 |
| 5×2.5 | 1 | 0.7 | 0.2 | 1.8 | 15.2 | 383 | 7.41 |
| 5×4 | 1 | 0.7 | 0.2 | 1.8 | 16.5 | 485 | 4.61 |
| 5×6 | 1 | 0.7 | 0.2 | 1.8 | 17.9 | 613 | 3.08 |
| 5×10 | 6 | 0.7 | 0.2 | 1.8 | 21.3 | 886 | 1.83 |
| 5×16 | 6 | 0.7 | 0.2 | 1.8 | 23.4 | 1212 | 1.15 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×25 | 6 | 0.9 | 0.2 | 1.8 | 27.8 | 1751 | 0.727 |
| 5×35 | 6 | 0.9 | 0.2 | 1.9 | 30.7 | 2277 | 0.524 |
| 5×50 | 6 | 1.0 | 0.2 | 2.0 | 35.6 | 3029 | 0.387 |
| 5×70 | 12 | 1.1 | 0.5 | 2.3 | 42.0 | 4551 | 0.268 |
| 5×95 | 15 | 1.1 | 0.5 | 2.4 | 47.5 | 6006 | 0.193 |
| 5×120 | 18 | 1.2 | 0.5 | 2.5 | 52.0 | 7354 | 0.153 |
| 5×150 | 18 | 1.4 | 0.5 | 2.7 | 57.9 | 8999 | 0.124 |
| 5×185 | 30 | 1.6 | 0.5 | 2.9 | 63.7 | 11074 | 0.0991 |
| 5×240 | 34 | 1.7 | 0.5 | 3.1 | 70.9 | 14042 | 0.0754 |
| 5×300 | 34 | 1.8 | 0.5 | 3.4 | 78.3 | 17364 | 0.0601 |
| 5×400 | 53 | 2.0 | 0.8 | 3.7 | 88.8 | 22823 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 14.1 | 322 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 15.2 | 399 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.4 | 499 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 19.0 | 694 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 21.2 | 949 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 24.6 | 1344 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.4 | 1653 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 0.2 | 1.9 | 30.3 | 2194 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 0.2 | 2.0 | 34.9 | 3005 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 0.5 | 2.2 | 40.7 | 4369 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.2/1.1 | 0.5 | 2.3 | 44.8 | 5424 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.4/1.1 | 0.5 | 2.5 | 49.1 | 6433 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 0.5 | 2.6 | 54.0 | 7959 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 1.7/1.2 | 0.5 | 2.8 | 60.3 | 10095 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 1.8/1.4 | 0.5 | 3.0 | 66.2 | 12359 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 0.5 | 3.2 | 74.0 | 15608 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 14.8 | 355 | 7.41/12.1 |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.0 | 444 | 4.61/7.41 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 17.3 | 562 | 3.08/4.61 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 19.9 | 776 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 22.6 | 1081 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.0 | 1532 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 27.7 | 1836 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 0.2 | 1.9 | 32.7 | 2525 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 0.2 | 2.1 | 36.9 | 3399 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 0.5 | 2.3 | 43.1 | 4917 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.2/1.1 | 0.5 | 2.4 | 48.1 | 6235 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.4/1.1 | 0.5 | 2.5 | 51.4 | 7165 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 0.5 | 2.7 | 57.4 | 9040 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 1.7/1.2 | 0.5 | 2.9 | 63.5 | 11363 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 1.8/1.4 | 0.5 | 3.1 | 69.9 | 13917 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 0.5 | 3.4 | 78.2 | 17581 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 15.0 | 369 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.2 | 464 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 17.6 | 587 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 20.6 | 831 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 23.0 | 1147 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.9 | 1641 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 29.1 | 2049 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 0.2 | 2.0 | 34.3 | 2783 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 0.5 | 2.2 | 40.1 | 4152 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 0.5 | 2.3 | 45.0 | 5427 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.2/1.1 | 0.5 | 2.5 | 50.1 | 6804 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.4/1.1 | 0.5 | 2.6 | 54.4 | 8047 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 0.5 | 2.8 | 60.5 | 10052 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 1.7/1.2 | 0.5 | 3.0 | 67.2 | 12697 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 1.8/1.4 | 0.5 | 3.2 | 74.2 | 15654 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 0.8 | 3.6 | 84.2 | 20594 | 0.0470/0.0991 |

YJLV22 (NA2XBY)  Multi-Core  0.6/1kV

AL/XLPE/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler: Non-hygroscopic material

- Binder: Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.7 | 0.2 | 1.8 | 13.0 | 228 | 12.1 |
| 2×4 | 1 | 0.7 | 0.2 | 1.8 | 14.0 | 260 | 7.41 |
| 2×6 | 1 | 0.7 | 0.2 | 1.8 | 15.0 | 300 | 4.61 |
| 2×10 | 6 | 0.7 | 0.2 | 1.8 | 17.5 | 373 | 3.08 |
| 2×16 | 6 | 0.7 | 0.2 | 1.8 | 19.1 | 461 | 1.91 |
| 2×25 | 6 | 0.9 | 0.2 | 1.8 | 22.3 | 609 | 1.20 |
| 2×35 | 6 | 0.9 | 0.2 | 1.8 | 24.3 | 722 | 0.868 |
| 2×50 | 6 | 1.0 | 0.2 | 1.8 | 27.3 | 874 | 0.641 |
| 2×70 | 12 | 1.1 | 0.2 | 1.9 | 30.9 | 1106 | 0.443 |
| 2×95 | 15 | 1.1 | 0.2 | 2.0 | 35.4 | 1433 | 0.320 |
| 2×120 | 15 | 1.2 | 0.5 | 2.2 | 40.2 | 2078 | 0.253 |
| 2×150 | 15 | 1.4 | 0.5 | 2.3 | 44.2 | 2465 | 0.206 |
| 2×185 | 30 | 1.6 | 0.5 | 2.5 | 49.0 | 2977 | 0.164 |
| 2×240 | 30 | 1.7 | 0.5 | 2.6 | 54.2 | 3603 | 0.125 |
| 2×300 | 30 | 1.8 | 0.5 | 2.8 | 59.8 | 4330 | 0.100 |
| 2×400 | 53 | 2.0 | 0.5 | 3.0 | 66.6 | 5268 | 0.0778 |
| 3×2.5 | 1 | 0.7 | 0.2 | 1.8 | 13.5 | 249 | 12.1 |
| 3×4 | 1 | 0.7 | 0.2 | 1.8 | 14.5 | 287 | 7.41 |
| 3×6 | 1 | 0.7 | 0.2 | 1.8 | 15.6 | 335 | 4.61 |
| 3×10 | 6 | 0.7 | 0.2 | 1.8 | 18.4 | 422 | 3.08 |
| 3×16 | 6 | 0.7 | 0.2 | 1.8 | 20.1 | 529 | 1.91 |
| 3×25 | 6 | 0.9 | 0.2 | 1.8 | 23.5 | 711 | 1.20 |
| 3X35 | 6 | 0.9 | 0.2 | 1.8 | 25.7 | 853 | 0.868 |
| 3×50 | 6 | 1.0 | 0.2 | 1.8 | 28.9 | 1045 | 0.641 |
| 3×70 | 12 | 1.1 | 0.2 | 2.0 | 33.7 | 1409 | 0.443 |
| 3×95 | 15 | 1.1 | 0.5 | 2.2 | 39.2 | 2153 | 0.320 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×120 | 15 | 1.2 | 0.5 | 2.3 | 42.9 | 2517 | 0.253 |
| 3×150 | 15 | 1.4 | 0.5 | 2.4 | 47.6 | 3043 | 0.206 |
| 3×185 | 30 | 1.6 | 0.5 | 2.6 | 52.3 | 3636 | 0.164 |
| 3×240 | 30 | 1.7 | 0.5 | 2.7 | 58.3 | 4504 | 0.125 |
| 3×300 | 30 | 1.8 | 0.5 | 2.9 | 63.9 | 5362 | 0.100 |
| 3×400 | 53 | 2.0 | 0.5 | 3.2 | 71.4 | 6602 | 0.0778 |
| 4×2.5 | 1 | 0.7 | 0.2 | 1.8 | 14.3 | 278 | 12.1 |
| 4×4 | 1 | 0.7 | 0.2 | 1.8 | 15.5 | 325 | 7.41 |
| 4×6 | 1 | 0.7 | 0.2 | 1.8 | 16.7 | 383 | 4.61 |
| 4×10 | 6 | 0.7 | 0.2 | 1.8 | 19.8 | 487 | 3.08 |
| 4×16 | 6 | 0.7 | 0.2 | 1.8 | 21.7 | 619 | 1.91 |
| 4×25 | 6 | 0.9 | 0.2 | 1.8 | 25.6 | 843 | 1.20 |
| 4×35 | 6 | 0.9 | 0.2 | 1.8 | 28.0 | 1021 | 0.868 |
| 4×50 | 6 | 1.0 | 0.2 | 1.9 | 31.8 | 1274 | 0.641 |
| 4×70 | 12 | 1.1 | 0.2 | 2.1 | 37.0 | 1723 | 0.443 |
| 4×95 | 15 | 1.1 | 0.5 | 2.3 | 43.0 | 2599 | 0.320 |
| 4×120 | 15 | 1.2 | 0.5 | 2.4 | 47.5 | 3100 | 0.253 |
| 4×150 | 15 | 1.4 | 0.5 | 2.6 | 52.5 | 3724 | 0.206 |
| 4×185 | 30 | 1.6 | 0.5 | 2.7 | 57.9 | 4503 | 0.164 |
| 4×240 | 30 | 1.7 | 0.5 | 2.9 | 64.4 | 5552 | 0.125 |
| 4×300 | 30 | 1.8 | 0.5 | 3.1 | 70.6 | 6634 | 0.100 |
| 4×400 | 53 | 2.0 | 0.5 | 3.4 | 79.3 | 8279 | 0.0778 |
| 5×2.5 | 1 | 0.7 | 0.2 | 1.8 | 15.2 | 311 | 12.1 |
| 5×4 | 1 | 0.7 | 0.2 | 1.8 | 16.5 | 365 | 7.41 |
| 5×6 | 1 | 0.7 | 0.2 | 1.8 | 17.9 | 434 | 4.61 |
| 5×10 | 6 | 0.7 | 0.2 | 1.8 | 21.3 | 558 | 3.08 |
| 5×16 | 6 | 0.7 | 0.2 | 1.8 | 23.4 | 717 | 1.91 |
| 5×25 | 6 | 0.9 | 0.2 | 1.8 | 27.8 | 985 | 1.20 |
| 5×35 | 6 | 0.9 | 0.2 | 1.9 | 30.7 | 1214 | 0.868 |
| 5×50 | 6 | 1.0 | 0.2 | 2.0 | 35.6 | 1571 | 0.641 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×70 | 12 | 1.1 | 0.5 | 2.3 | 42.0 | 2470 | 0.443 |
| 5×95 | 15 | 1.1 | 0.5 | 2.4 | 47.5 | 3121 | 0.320 |
| 5×120 | 15 | 1.2 | 0.5 | 2.5 | 52.0 | 3677 | 0.253 |
| 5×150 | 15 | 1.4 | 0.5 | 2.7 | 57.9 | 4489 | 0.206 |
| 5×185 | 30 | 1.6 | 0.5 | 2.9 | 63.7 | 5393 | 0.164 |
| 5×240 | 30 | 1.7 | 0.5 | 3.1 | 70.9 | 6670 | 0.125 |
| 5×300 | 30 | 1.8 | 0.5 | 3.4 | 78.3 | 8106 | 0.100 |
| 5×400 | 53 | 2.0 | 0.8 | 3.7 | 88.8 | 10874 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 15.2 | 313 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.4 | 368 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 19.0 | 461 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 21.2 | 586 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 24.6 | 786 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.4 | 917 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 0.2 | 1.9 | 30.3 | 1166 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 0.2 | 2.0 | 34.9 | 1545 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 0.5 | 2.2 | 40.7 | 2344 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.2/1.1 | 0.5 | 2.3 | 44.8 | 2801 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.4/1.1 | 0.5 | 2.5 | 49.1 | 3311 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 0.5 | 2.6 | 54.0 | 3974 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 1.7/1.2 | 0.5 | 2.8 | 60.3 | 4934 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 1.8/1.4 | 0.5 | 3.0 | 66.2 | 5903 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 0.5 | 3.2 | 74.0 | 7306 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.0 | 343 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 17.3 | 406 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 19.9 | 508 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 22.6 | 653 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.0 | 875 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 27.7 | 1001 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 0.2 | 1.9 | 32.7 | 1332 | 0.641/1.20 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 0.2 | 2.1 | 36.9 | 1726 | 0.443/0.868 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 0.5 | 2.3 | 43.1 | 2599 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.2/1.1 | 0.5 | 2.4 | 48.1 | 3198 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.4/1.1 | 0.5 | 2.5 | 51.4 | 3627 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 0.5 | 2.7 | 57.4 | 4478 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 1.7/1.2 | 0.5 | 2.9 | 63.5 | 5467 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 1.8/1.4 | 0.5 | 3.1 | 69.9 | 6560 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 0.5 | 3.4 | 78.2 | 8146 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 16.2 | 354 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 0.2 | 1.8 | 17.6 | 420 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 0.2 | 1.8 | 20.6 | 533 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 0.2 | 1.8 | 23.0 | 684 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 26.9 | 930 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 0.2 | 1.8 | 29.1 | 1100 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 0.2 | 2.0 | 34.3 | 1464 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 0.5 | 2.2 | 40.1 | 2275 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 0.5 | 2.3 | 45.0 | 2825 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.2/1.1 | 0.5 | 2.5 | 50.1 | 3447 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.4/1.1 | 0.5 | 2.6 | 54.4 | 4023 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 0.5 | 2.8 | 60.5 | 4931 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 1.7/1.2 | 0.5 | 3.0 | 67.2 | 6062 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 1.8/1.4 | 0.5 | 3.2 | 74.2 | 7346 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 0.8 | 3.6 | 84.2 | 9900 | 0.0778/0.164 |

YJV72 (N2XRY)  Single Core  0.6/1kV

CU/XLPE/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Inner sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magneticsteel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 0.7 | 0.8 | 1.4 | 12.1 | 322 | 1.83 |
| 1×16 | 6 | 0.7 | 0.8 | 1.4 | 12.9 | 397 | 1.15 |
| 1×25 | 6 | 0.9 | 0.8 | 1.4 | 14.5 | 526 | 0.727 |
| 1×35 | 6 | 0.9 | 0.8 | 1.4 | 15.5 | 642 | 0.524 |
| 1×50 | 6 | 1.0 | 1.25 | 1.5 | 18.1 | 920 | 0.387 |
| 1×70 | 12 | 1.1 | 1.25 | 1.5 | 19.8 | 1181 | 0.268 |
| 1×95 | 15 | 1.1 | 1.25 | 1.6 | 21.8 | 1488 | 0.193 |
| 1×120 | 18 | 1.2 | 1.6 | 1.7 | 24.3 | 1922 | 0.153 |
| 1×150 | 18 | 1.4 | 1.6 | 1.7 | 26.2 | 2253 | 0.124 |
| 1×185 | 30 | 1.6 | 1.6 | 1.8 | 28.4 | 2705 | 0.0991 |
| 1×240 | 34 | 1.7 | 1.6 | 1.9 | 31.1 | 3343 | 0.0754 |
| 1×300 | 34 | 1.8 | 1.6 | 2.0 | 33.7 | 4011 | 0.0601 |
| 1×400 | 53 | 2.0 | 2.0 | 2.1 | 38.3 | 5273 | 0.0470 |
| 1×500 | 53 | 2.2 | 2.0 | 2.2 | 41.8 | 6426 | 0.0366 |
| 1×630 | 53 | 2.4 | 2.0 | 2.3 | 46.1 | 7990 | 0.0283 |

YJLV72 (NA2XRY)  Single Core  0.6/1kV

AL/XLPE/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Inner sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magneticsteel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 0.7 | 0.8 | 1.4 | 12.1 | 253 | 3.08 |
| 1×16 | 6 | 0.7 | 0.8 | 1.4 | 12.9 | 299 | 1.91 |
| 1×25 | 6 | 0.9 | 0.8 | 1.4 | 14.5 | 374 | 1.20 |
| 1×35 | 6 | 0.9 | 0.8 | 1.4 | 15.5 | 430 | 0.868 |
| 1×50 | 6 | 1.0 | 1.25 | 1.5 | 18.1 | 630 | 0.641 |
| 1×70 | 12 | 1.1 | 1.25 | 1.5 | 19.8 | 767 | 0.443 |
| 1×95 | 15 | 1.1 | 1.25 | 1.6 | 21.8 | 914 | 0.320 |
| 1×120 | 15 | 1.2 | 1.6 | 1.7 | 24.3 | 1176 | 0.253 |
| 1×150 | 15 | 1.4 | 1.6 | 1.7 | 26.2 | 1356 | 0.206 |
| 1×185 | 30 | 1.6 | 1.6 | 1.8 | 28.4 | 1575 | 0.164 |
| 1×240 | 30 | 1.7 | 1.6 | 1.9 | 31.1 | 1876 | 0.125 |
| 1×300 | 30 | 1.8 | 1.6 | 2.0 | 33.7 | 2170 | 0.100 |
| 1×400 | 53 | 2.0 | 2.0 | 2.1 | 38.3 | 2875 | 0.0778 |
| 1×500 | 53 | 2.2 | 2.0 | 2.2 | 41.8 | 3419 | 0.0605 |
| 1×630 | 53 | 2.4 | 2.0 | 2.3 | 46.1 | 4085 | 0.0469 |

YJV32 (N2XRY)  Multi- Core  0.6/1kV

CU/XLPE/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Copper  ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE N2XRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.7 | 0.8 | 1.8 | 13.3 | 300 | 12.1 |
| 2×2.5 | 1 | 0.7 | 0.8 | 1.8 | 14.1 | 343 | 7.41 |
| 2×4 | 1 | 0.7 | 0.8 | 1.8 | 15.1 | 404 | 4.61 |
| 2×6 | 1 | 0.7 | 0.8 | 1.8 | 16.1 | 476 | 3.08 |
| 2×10 | 6 | 0.7 | 1.25 | 1.8 | 19.5 | 763 | 1.83 |
| 2×16 | 6 | 0.7 | 1.25 | 1.8 | 21.1 | 942 | 1.15 |
| 2×25 | 6 | 0.9 | 1.6 | 1.8 | 25.0 | 1384 | 0.727 |
| 2×35 | 6 | 0.9 | 1.6 | 1.8 | 27.0 | 1668 | 0.524 |
| 2×50 | 6 | 1.0 | 1.6 | 1.8 | 30.0 | 2061 | 0.387 |
| 2×70 | 12 | 1.1 | 1.6 | 2.0 | 33.8 | 2628 | 0.268 |
| 2×95 | 15 | 1.1 | 2.0 | 2.1 | 39.1 | 3649 | 0.193 |
| 2×120 | 18 | 1.2 | 2.0 | 2.2 | 42.5 | 4334 | 0.153 |
| 2×150 | 18 | 1.4 | 2.0 | 2.3 | 46.5 | 5134 | 0.124 |
| 2×185 | 30 | 1.6 | 2.5 | 2.5 | 52.3 | 6658 | 0.0991 |
| 2×240 | 34 | 1.7 | 2.5 | 2.7 | 57.7 | 8140 | 0.0754 |
| 2×300 | 34 | 1.8 | 2.5 | 2.8 | 63.1 | 9754 | 0.0601 |
| 2×400 | 53 | 2.0 | 2.5 | 3.1 | 70.1 | 12015 | 0.0470 |
| 3×1.5 | 1 | 0.7 | 0.8 | 1.8 | 13.8 | 331 | 12.1 |
| 3×2.5 | 1 | 0.7 | 0.8 | 1.8 | 14.6 | 384 | 7.41 |
| 3×4 | 1 | 0.7 | 0.8 | 1.8 | 15.6 | 460 | 4.61 |
| 3×6 | 1 | 0.7 | 0.8 | 1.8 | 16.7 | 552 | 3.08 |
| 3×10 | 6 | 0.7 | 1.25 | 1.8 | 20.4 | 889 | 1.83 |
| 3×16 | 6 | 0.7 | 1.25 | 1.8 | 22.1 | 1133 | 1.15 |
| 3×25 | 6 | 0.9 | 1.6 | 1.8 | 26.2 | 1680 | 0.727 |
| 3X35 | 6 | 0.9 | 1.6 | 1.8 | 28.4 | 2051 | 0.524 |
| 3×50 | 6 | 1.0 | 1.6 | 1.9 | 31.8 | 2572 | 0.387 |
| 3×70 | 12 | 1.1 | 2.0 | 2.0 | 37.2 | 3637 | 0.268 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×95 | 15 | 1.1 | 2.0 | 2.2 | 41.5 | 4626 | 0.193 |
| 3×120 | 18 | 1.2 | 2.0 | 2.3 | 45.2 | 5565 | 0.153 |
| 3×150 | 18 | 1.4 | 2.5 | 2.5 | 51.1 | 7121 | 0.124 |
| 3×185 | 30 | 1.6 | 2.5 | 2.6 | 55.6 | 8522 | 0.0991 |
| 3×240 | 34 | 1.7 | 2.5 | 2.8 | 61.8 | 10612 | 0.0754 |
| 3×300 | 34 | 1.8 | 2.5 | 3.0 | 67.4 | 12798 | 0.0601 |
| 3×400 | 53 | 2.0 | 2.5 | 3.2 | 74.7 | 15826 | 0.0470 |
| 4×1.5 | 1 | 0.7 | 0.8 | 1.8 | 14.5 | 372 | 12.1 |
| 4×2.5 | 1 | 0.7 | 0.8 | 1.8 | 15.4 | 435 | 7.41 |
| 4×4 | 1 | 0.7 | 0.8 | 1.8 | 16.6 | 531 | 4.61 |
| 4×6 | 1 | 0.7 | 1.25 | 1.8 | 18.7 | 765 | 3.08 |
| 4×10 | 6 | 0.7 | 1.25 | 1.8 | 21.8 | 1049 | 1.83 |
| 4×16 | 6 | 0.7 | 1.6 | 1.8 | 24.4 | 1473 | 1.15 |
| 4×25 | 6 | 0.9 | 1.6 | 1.8 | 28.3 | 2017 | 0.727 |
| 4×35 | 6 | 0.9 | 1.6 | 1.9 | 30.9 | 2495 | 0.524 |
| 4×50 | 6 | 1.0 | 1.6 | 2.0 | 34.7 | 3157 | 0.387 |
| 4×70 | 12 | 1.1 | 2.0 | 2.2 | 40.7 | 4493 | 0.268 |
| 4×95 | 15 | 1.1 | 2.0 | 2.3 | 45.3 | 5742 | 0.193 |
| 4×120 | 18 | 1.2 | 2.5 | 2.5 | 51.0 | 7417 | 0.153 |
| 4×150 | 18 | 1.4 | 2.5 | 2.6 | 55.8 | 8806 | 0.124 |
| 4×185 | 30 | 1.6 | 2.5 | 2.8 | 61.4 | 10739 | 0.0991 |
| 4×240 | 34 | 1.7 | 2.5 | 3.0 | 67.9 | 13321 | 0.0754 |
| 4×300 | 34 | 1.8 | 2.5 | 3.2 | 74.1 | 16097 | 0.0601 |
| 4×400 | 53 | 2.0 | 3.15 | 3.5 | 84.1 | 21074 | 0.0470 |
| 5×1.5 | 1 | 0.7 | 0.8 | 1.8 | 15.3 | 414 | 12.1 |
| 5×2.5 | 1 | 0.7 | 0.8 | 1.8 | 16.3 | 492 | 7.41 |
| 5×4 | 1 | 0.7 | 1.25 | 1.8 | 18.5 | 726 | 4.61 |
| 5×6 | 1 | 0.7 | 1.25 | 1.8 | 19.9 | 874 | 3.08 |
| 5×10 | 6 | 0.7 | 1.25 | 1.8 | 23.3 | 1214 | 1.83 |
| 5×16 | 6 | 0.7 | 1.6 | 1.8 | 26.1 | 1723 | 1.15 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×25 | 6 | 0.9 | 1.6 | 1.8 | 30.5 | 2362 | 0.727 |
| 5×35 | 6 | 0.9 | 1.6 | 1.9 | 33.4 | 2953 | 0.524 |
| 5×50 | 6 | 1.0 | 2.0 | 2.1 | 39.3 | 4090 | 0.387 |
| 5×70 | 12 | 1.1 | 2.0 | 2.3 | 44.3 | 5352 | 0.268 |
| 5×95 | 15 | 1.1 | 2.5 | 2.5 | 51.0 | 7379 | 0.193 |
| 5×120 | 18 | 1.2 | 2.5 | 2.6 | 55.5 | 8856 | 0.153 |
| 5×150 | 18 | 1.4 | 2.5 | 2.8 | 61.4 | 10690 | 0.124 |
| 5×185 | 30 | 1.6 | 2.5 | 3.0 | 67.2 | 12917 | 0.0991 |
| 5×240 | 34 | 1.7 | 2.5 | 3.2 | 74.4 | 16133 | 0.0754 |
| 5×300 | 34 | 1.8 | 3.15 | 3.4 | 82.9 | 20582 | 0.0601 |
| 5×400 | 53 | 2.0 | 3.15 | 3.8 | 92.4 | 25587 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.7/0.7 | 0.8 | 1.8 | 15.2 | 418 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 0.8 | 1.8 | 16.3 | 508 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.4 | 740 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 21.0 | 977 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 1.25 | 1.8 | 23.2 | 1268 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 27.3 | 1879 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 29.1 | 2225 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 1.6 | 1.9 | 33.0 | 2856 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 2.0 | 2.1 | 38.6 | 4045 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 2.0 | 2.2 | 43.0 | 5162 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.2/1.1 | 2.0 | 2.4 | 47.3 | 6325 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.4/1.1 | 2.5 | 2.5 | 52.4 | 7841 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 2.7 | 57.5 | 9512 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 1.7/1.2 | 2.5 | 2.9 | 63.8 | 11870 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 1.8/1.4 | 2.5 | 3.0 | 69.5 | 14254 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 3.15 | 3.3 | 78.8 | 18672 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.7/0.7 | 0.8 | 1.8 | 15.9 | 459 | 7.41/12.1 |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.0 | 678 | 4.61/7.41 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 19.3 | 817 | 3.08/4.61 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 21.9 | 1073 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 1.6 | 1.8 | 25.3 | 1565 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 28.7 | 2106 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 30.4 | 2448 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 2.0 | 2.0 | 36.4 | 3499 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 2.0 | 2.1 | 40.4 | 4487 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 2.0 | 2.3 | 45.4 | 5750 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.2/1.1 | 2.5 | 2.5 | 51.6 | 7638 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.4/1.1 | 2.5 | 2.6 | 54.9 | 8637 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 2.5 | 2.8 | 60.9 | 10700 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 1.7/1.2 | 2.5 | 3.0 | 67.0 | 13208 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 1.8/1.4 | 2.5 | 3.2 | 73.4 | 15945 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 3.15 | 3.5 | 83.0 | 20775 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.7/0.7 | 0.8 | 1.8 | 16.1 | 476 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.2 | 697 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 19.6 | 850 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 22.6 | 1143 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 1.6 | 1.8 | 25.7 | 1644 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 29.6 | 2226 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.9 | 32.0 | 2698 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 2.0 | 2.1 | 38.0 | 3802 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 2.0 | 2.2 | 42.4 | 4931 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 2.0 | 2.4 | 47.5 | 6325 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.2/1.1 | 2.5 | 2.5 | 53.4 | 8233 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.4/1.1 | 2.5 | 2.7 | 57.9 | 9632 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 2.9 | 64.0 | 11824 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 1.7/1.2 | 2.5 | 3.1 | 70.7 | 14645 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 1.8/1.4 | 3.15 | 3.3 | 79.0 | 18714 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 3.15 | 3.6 | 87.6 | 23183 | 0.0470/0.0991 |

YJLV32 (NA2XRY)  Multi- Core  0.6/1kV

AL/XLPE/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Cross-linked polyethylene XLPE

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERRISTICS

Good electrical and mechanical properties. Cross-linked polyethylene insulation allows greater power capacity under any operating condition, minimum dielectric losses, high insulation resistance. The PVC outer sheath allows an adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NA2XRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.7 | 0.8 | 1.8 | 14.1 | 314 | 12.1 |
| 2×4 | 1 | 0.7 | 0.8 | 1.8 | 15.1 | 357 | 7.41 |
| 2×6 | 1 | 0.7 | 0.8 | 1.8 | 16.1 | 406 | 4.61 |
| 2×10 | 6 | 0.7 | 1.25 | 1.8 | 19.5 | 619 | 3.08 |
| 2×16 | 6 | 0.7 | 1.25 | 1.8 | 21.1 | 743 | 1.91 |
| 2×25 | 6 | 0.9 | 1.6 | 1.8 | 25.0 | 1078 | 1.20 |
| 2×35 | 6 | 0.9 | 1.6 | 1.8 | 27.0 | 1243 | 0.868 |
| 2×50 | 6 | 1.0 | 1.6 | 1.8 | 30.0 | 1459 | 0.641 |
| 2×70 | 12 | 1.1 | 1.6 | 2.0 | 33.8 | 1796 | 0.443 |
| 2×95 | 15 | 1.1 | 2.0 | 2.1 | 39.1 | 2495 | 0.320 |
| 2×120 | 15 | 1.2 | 2.0 | 2.2 | 42.5 | 2836 | 0.253 |
| 2×150 | 15 | 1.4 | 2.0 | 2.3 | 46.5 | 3330 | 0.206 |
| 2×185 | 30 | 1.6 | 2.5 | 2.5 | 52.3 | 4386 | 0.164 |
| 2×240 | 30 | 1.7 | 2.5 | 2.7 | 57.7 | 5192 | 0.125 |
| 2×300 | 30 | 1.8 | 2.5 | 2.8 | 63.1 | 6049 | 0.100 |
| 2×400 | 53 | 2.0 | 2.5 | 3.1 | 70.1 | 7194 | 0.0778 |
| 3×2.5 | 1 | 0.7 | 0.8 | 1.8 | 14.6 | 340 | 12.1 |
| 3×4 | 1 | 0.7 | 0.8 | 1.8 | 15.6 | 388 | 7.41 |
| 3×6 | 1 | 0.7 | 0.8 | 1.8 | 16.7 | 448 | 4.61 |
| 3×10 | 6 | 0.7 | 1.25 | 1.8 | 20.4 | 682 | 3.08 |
| 3×16 | 6 | 0.7 | 1.25 | 1.8 | 22.1 | 835 | 1.91 |
| 3×25 | 6 | 0.9 | 1.6 | 1.8 | 26.2 | 1221 | 1.20 |
| 3X35 | 6 | 0.9 | 1.6 | 1.8 | 28.4 | 1414 | 0.868 |
| 3×50 | 6 | 1.0 | 1.6 | 1.9 | 31.8 | 1681 | 0.641 |
| 3×70 | 12 | 1.1 | 2.0 | 2.0 | 37.2 | 2389 | 0.443 |
| 3×95 | 15 | 1.1 | 2.0 | 2.2 | 41.5 | 2895 | 0.320 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×120 | 15 | 1.2 | 2.0 | 2.3 | 45.2 | 3336 | 0.253 |
| 3×150 | 15 | 1.4 | 2.5 | 2.5 | 51.1 | 4415 | 0.206 |
| 3×185 | 30 | 1.6 | 2.5 | 2.6 | 55.6 | 5113 | 0.164 |
| 3×240 | 30 | 1.7 | 2.5 | 2.8 | 61.8 | 6188 | 0.125 |
| 3×300 | 30 | 1.8 | 2.5 | 3.0 | 67.4 | 7206 | 0.100 |
| 3×400 | 53 | 2.0 | 2.5 | 3.2 | 74.7 | 8623 | 0.0778 |
| 4×2.5 | 1 | 0.7 | 0.8 | 1.8 | 15.4 | 377 | 12.1 |
| 4×4 | 1 | 0.7 | 0.8 | 1.8 | 16.6 | 436 | 7.41 |
| 4×6 | 1 | 0.7 | 1.25 | 1.8 | 18.7 | 631 | 4.61 |
| 4×10 | 6 | 0.7 | 1.25 | 1.8 | 21.8 | 779 | 3.08 |
| 4×16 | 6 | 0.7 | 1.6 | 1.8 | 24.4 | 1076 | 1.91 |
| 4×25 | 6 | 0.9 | 1.6 | 1.8 | 28.3 | 1404 | 1.20 |
| 4×35 | 6 | 0.9 | 1.6 | 1.9 | 30.9 | 1645 | 0.868 |
| 4×50 | 6 | 1.0 | 1.6 | 2.0 | 34.7 | 1977 | 0.641 |
| 4×70 | 12 | 1.1 | 2.0 | 2.2 | 40.7 | 2829 | 0.443 |
| 4×95 | 15 | 1.1 | 2.0 | 2.3 | 45.3 | 3434 | 0.320 |
| 4×120 | 15 | 1.2 | 2.5 | 2.5 | 51.0 | 4442 | 0.253 |
| 4×150 | 15 | 1.4 | 2.5 | 2.6 | 55.8 | 5198 | 0.206 |
| 4×185 | 30 | 1.6 | 2.5 | 2.8 | 61.4 | 6194 | 0.164 |
| 4×240 | 30 | 1.7 | 2.5 | 3.0 | 67.9 | 7424 | 0.125 |
| 4×300 | 30 | 1.8 | 2.5 | 3.2 | 74.1 | 8695 | 0.100 |
| 4×400 | 53 | 2.0 | 3.15 | 3.5 | 84.1 | 11526 | 0.0778 |
| 5×2.5 | 1 | 0.7 | 0.8 | 1.8 | 16.3 | 419 | 12.1 |
| 5×4 | 1 | 0.7 | 1.25 | 1.8 | 18.5 | 606 | 7.41 |
| 5×6 | 1 | 0.7 | 1.25 | 1.8 | 19.9 | 704 | 4.61 |
| 5×10 | 6 | 0.7 | 1.25 | 1.8 | 23.3 | 870 | 3.08 |
| 5×16 | 6 | 0.7 | 1.6 | 1.8 | 26.1 | 1227 | 1.91 |
| 5×25 | 6 | 0.9 | 1.6 | 1.8 | 30.5 | 1597 | 1.20 |
| 5×35 | 6 | 0.9 | 1.6 | 1.9 | 33.4 | 1890 | 0.868 |
| 5×50 | 6 | 1.0 | 2.0 | 2.1 | 39.3 | 2609 | 0.641 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×70 | 12 | 1.1 | 2.0 | 2.3 | 44.3 | 3271 | 0.443 |
| 5×95 | 15 | 1.1 | 2.5 | 2.5 | 51.0 | 4494 | 0.320 |
| 5×120 | 15 | 1.2 | 2.5 | 2.6 | 55.5 | 5148 | 0.253 |
| 5×150 | 15 | 1.4 | 2.5 | 2.8 | 61.4 | 6181 | 0.206 |
| 5×185 | 30 | 1.6 | 2.5 | 3.0 | 67.2 | 7236 | 0.164 |
| 5×240 | 30 | 1.7 | 2.5 | 3.2 | 74.4 | 8761 | 0.125 |
| 5×300 | 30 | 1.8 | 3.15 | 3.4 | 82.9 | 11266 | 0.100 |
| 5×400 | 53 | 2.0 | 3.15 | 3.8 | 92.4 | 13590 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 0.7/0.7 | 0.8 | 1.8 | 16.3 | 422 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.4 | 608 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 21.0 | 736 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 0.7/0.7 | 1.25 | 1.8 | 23.2 | 905 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 27.3 | 1321 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 29.1 | 1489 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.0/0.9 | 1.6 | 1.9 | 33.0 | 1831 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.1/0.9 | 2.0 | 2.1 | 38.6 | 2584 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.1/1.0 | 2.0 | 2.2 | 43.0 | 3114 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.2/1.1 | 2.0 | 2.4 | 47.3 | 3683 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.4/1.1 | 2.5 | 2.5 | 52.4 | 4719 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 2.7 | 57.5 | 5527 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 1.7/1.2 | 2.5 | 2.9 | 63.8 | 6672 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 1.8/1.4 | 2.5 | 3.0 | 69.5 | 7800 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.0/1.6 | 3.15 | 3.3 | 78.8 | 10313 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.0 | 577 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 19.3 | 660 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 21.9 | 807 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 0.7/0.7 | 1.6 | 1.8 | 25.3 | 1138 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 28.7 | 1450 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 30.4 | 1614 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.0/0.9 | 2.0 | 2.0 | 36.4 | 2285 | 0.641/1.20 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×70+2×35 | 12/6 | 1.1/0.9 | 2.0 | 2.1 | 40.4 | 2814 | 0.443/0.868 |
| 3×95+2×50 | 15/6 | 1.1/1.0 | 2.0 | 2.3 | 45.4 | 3436 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.2/1.1 | 2.5 | 2.5 | 51.6 | 4566 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.4/1.1 | 2.5 | 2.6 | 54.9 | 5099 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 1.6/1.1 | 2.5 | 2.8 | 60.9 | 6138 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 1.7/1.2 | 2.5 | 3.0 | 67.0 | 7316 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 1.8/1.4 | 2.5 | 3.2 | 73.4 | 8591 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.0/1.6 | 3.15 | 3.5 | 83.0 | 11345 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 18.2 | 587 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 0.7/0.7 | 1.25 | 1.8 | 19.6 | 682 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 0.7/0.7 | 1.25 | 1.8 | 22.6 | 838 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 0.7/0.7 | 1.6 | 1.8 | 25.7 | 1182 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.8 | 29.6 | 1515 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 0.9/0.7 | 1.6 | 1.9 | 32.0 | 1750 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.0/0.9 | 2.0 | 2.1 | 38.0 | 2485 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.1/0.9 | 2.0 | 2.2 | 42.4 | 3054 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.1/1.0 | 2.0 | 2.4 | 47.5 | 3726 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.2/1.1 | 2.5 | 2.5 | 53.4 | 4843 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.4/1.1 | 2.5 | 2.7 | 57.9 | 5608 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 1.6/1.1 | 2.5 | 2.9 | 64.0 | 6702 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 1.7/1.2 | 2.5 | 3.1 | 70.7 | 8012 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 1.8/1.4 | 3.15 | 3.3 | 79.0 | 10410 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.0/1.6 | 3.15 | 3.6 | 87.6 | 12438 | 0.0778/0.164 |

Current rating (in accordance with IEC 60287)

The Current rating  is calculated according to the following conditions. One multi-core cables or one three phase group of single-core cables.

Maximum conductor temperature: 90℃

Temperature of the ground : 25℃

Temperature of ambient air : 40℃

Laying depth : 0.7m

Thermal resistivity of the ground : 1.0K·m/W

Spacing between cable laid: In flat formation 2 times of cable overall diameter,

In trefoil with cable touching.

Where the site conditions differ from the standard conditions mentioned, it will be necessary to multiply the tabulated ratings by the actors given in the following tables. These factors are for variation in ambient air temperature,in ambient ground temperature and soil thermal resistivity.

- Rating Factors

Cables laid direct in air:

Correction factors for ambient air temperatures other than 40 °C.

| Maximum conductor temperature °C | Ambient air temperature °C |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 |
| 90 | 1.23 | 1.17 | 1.12 | 1.06 | 1.00 | 0.94 | 0.87 | 0.81 |

Cables laid direct in ground:

Correction factors for ambient ground temperatures other than 25 °C.

| Maximum conductor temperature °C | Ambient ground temperature °C |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 10 | 15 | 20 | 25 | 30 | 35 |
| 90 | 1.11 | 1.07 | 1.04 | 1.00 | 0.96 | 0.92 |

The correction factors of current capacity for different soil thermal resistivity.

| Values of soil thermal resistivity K·m/W | 0.8 | 1.0 | 1.2 | 1.5 |
| --- | --- | --- | --- | --- |
| The Correction Factors of Current Capacity | 1.08 | 1.00 | 0.95 | 0.77 |

Current ratings for single-core cables

| Arrangement | Trefoil |  |  |  | Flat spaced |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 24 | -- | 33 | -- | 32 | -- | 36 | -- |
| 2.5 | 31 | 24 | 42 | 33 | 41 | 32 | 46 | 36 |
| 4 | 41 | 32 | 55 | 43 | 54 | 42 | 59 | 47 |
| 6 | 52 | 42 | 69 | 56 | 68 | 56 | 74 | 60 |
| 10 | 71 | 55 | 92 | 71 | 93 | 72 | 98 | 75 |
| 16 | 92 | 71 | 115 | 91 | 120 | 93 | 125 | 97 |
| 25 | 120 | 94 | 150 | 115 | 155 | 120 | 160 | 125 |
| 35 | 150 | 115 | 180 | 140 | 195 | 150 | 190 | 150 |
| 50 | 180 | 140 | 215 | 165 | 235 | 180 | 230 | 175 |
| 70 | 230 | 180 | 265 | 205 | 295 | 230 | 280 | 215 |
| 95 | 285 | 220 | 320 | 245 | 370 | 285 | 335 | 260 |
| 120 | 335 | 260 | 360 | 280 | 430 | 330 | 385 | 295 |
| 150 | 385 | 300 | 410 | 315 | 495 | 380 | 430 | 335 |
| 185 | 450 | 350 | 460 | 360 | 570 | 445 | 490 | 380 |
| 240 | 535 | 414 | 535 | 420 | 680 | 530 | 570 | 445 |
| 300 | 620 | 485 | 605 | 475 | 790 | 615 | 645 | 505 |
| 400 | 720 | 570 | 685 | 545 | 920 | 720 | 735 | 575 |
| 500 | 835 | 670 | 775 | 620 | 1080 | 850 | 840 | 665 |
| 630 | 960 | 790 | 865 | 705 | 1260 | 1000 | 950 | 760 |

Current ratings for multi-core un-armoured cables

| Arrangement | Two-core |  |  |  | Three-core and above |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 24 | -- | 35 | -- | 21 | -- | 30 | -- |
| 2.5 | 33 | 25 | 46 | 36 | 28 | 22 | 39 | 31 |
| 4 | 43 | 34 | 59 | 47 | 37 | 29 | 51 | 40 |
| 6 | 55 | 45 | 75 | 61 | 47 | 39 | 64 | 52 |
| 10 | 76 | 58 | 100 | 78 | 65 | 50 | 86 | 66 |
| 16 | 97 | 75 | 130 | 100 | 84 | 65 | 110 | 85 |
| 25 | 130 | 100 | 165 | 130 | 110 | 87 | 140 | 110 |
| 35 | 160 | 120 | 200 | 155 | 135 | 105 | 170 | 130 |
| 50 | 195 | 150 | 240 | 185 | 170 | 130 | 205 | 160 |
| 70 | 245 | 190 | 290 | 225 | 215 | 165 | 250 | 195 |
| 95 | 305 | 235 | 355 | 275 | 265 | 205 | 300 | 235 |
| 120 | 355 | 275 | 405 | 315 | 310 | 240 | 345 | 265 |
| 150 | 405 | 315 | 450 | 350 | 350 | 270 | 385 | 300 |
| 185 | 465 | 365 | 510 | 395 | 405 | 315 | 435 | 340 |
| 240 | -- | -- | -- | -- | 480 | 375 | 500 | 395 |
| 300 | -- | -- | -- | -- | 555 | 435 | 565 | 445 |
| 400 | -- | -- | -- | -- | 640 | 510 | 640 | 510 |

Current ratings for multi-core armoured cables

| Arrangement | Two-core |  |  |  | Three-core and above |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 24 | -- | 34 | -- | 20 | -- | 29 | -- |
| 2.5 | 33 | 25 | 45 | 35 | 26 | 21 | 35 | 30 |
| 4 | 43 | 34 | 59 | 47 | 35 | 28 | 50 | 40 |
| 6 | 55 | 45 | 74 | 61 | 45 | 35 | 60 | 50 |
| 10 | 75 | 58 | 100 | 77 | 64 | 50 | 85 | 65 |
| 16 | 97 | 75 | 135 | 105 | 83 | 64 | 110 | 85 |
| 25 | 125 | 100 | 165 | 130 | 110 | 86 | 140 | 110 |
| 35 | 155 | 120 | 200 | 155 | 135 | 105 | 170 | 130 |
| 50 | 190 | 145 | 240 | 185 | 165 | 125 | 200 | 150 |
| 70 | 245 | 190 | 295 | 230 | 210 | 165 | 245 | 190 |
| 95 | 300 | 235 | 355 | 275 | 260 | 200 | 300 | 230 |
| 120 | 350 | 270 | 405 | 315 | 305 | 235 | 335 | 260 |
| 150 | 400 | 310 | 455 | 355 | 345 | 270 | 380 | 295 |
| 185 | 460 | 355 | 515 | 400 | 395 | 310 | 430 | 335 |
| 240 | -- | -- | -- | -- | 465 | 365 | 500 | 390 |
| 300 | -- | -- | -- | -- | 535 | 420 | 565 | 440 |
| 400 | -- | -- | -- | -- | 620 | 495 | 650 | 505 |

Short Circuit Current

Short circuit current of XLPE insulated cable conductor is calculated according to IEC 60949,IEC 60724. Initial temperature is 90˚C,final temperature is 250˚C.

| Nominal area of conductor | Short circuit current (kA). Time |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Copper conductors |  |  | Aluminum conductors |  |  |
| mm2 | 1sec | 2sec | 3sec | 1sec | 2sec | 3sec |
| 1.5 | 0.21 | 0.15 | 0.12 | 0.14 | 0.10 | 0.08 |
| 2.5 | 0.36 | 0.25 | 0.21 | 0.24 | 0.17 | 0.14 |
| 4 | 0.57 | 0.40 | 0.33 | 0.38 | 0.27 | 0.22 |
| 6 | 0.86 | 0.61 | 0.50 | 0.57 | 0.40 | 0.33 |
| 10 | 1.43 | 1.01 | 0.83 | 0.94 | 0.67 | 0.55 |
| 16 | 2.29 | 1.62 | 1.32 | 1.51 | 1.07 | 0.87 |
| 25 | 3.6 | 2.5 | 2.1 | 2.4 | 1.7 | 1.4 |
| 35 | 5.0 | 3.5 | 2.9 | 3.3 | 2.3 | 1.9 |
| 50 | 7.2 | 5.1 | 4.1 | 4.7 | 3.3 | 2.7 |
| 70 | 10.0 | 7.1 | 5.8 | 6.6 | 4.7 | 3.8 |
| 95 | 13.6 | 9.6 | 7.8 | 9.0 | 6.3 | 5.2 |
| 120 | 17.2 | 12.1 | 9.9 | 11.3 | 8.0 | 6.5 |
| 150 | 21.5 | 15.2 | 12.4 | 14.2 | 10.0 | 8.2 |
| 185 | 26.5 | 18.7 | 15.3 | 17.5 | 12.4 | 10.1 |
| 240 | 34.3 | 24.3 | 19.8 | 22.7 | 16.0 | 13.1 |
| 300 | 42.9 | 30.4 | 24.8 | 28.3 | 20.0 | 16.4 |
| 400 | 57.2 | 40.5 | 33.0 | 37.8 | 26.7 | 21.8 |
| 500 | 71.5 | 50.6 | 41.3 | 47.2 | 33.4 | 27.3 |
| 630 | 90.1 | 63.7 | 52.0 | 59.5 | 42.1 | 34.4 |

0.6/1kV PVC Insulated Power Cables

APPLICATION

The products are used for electrical power transmission and distribution systems, operating at A.C. rated voltage of(U0/U) 0.6/1kV and below.These cables are suitable for electricity supply in low voltage distribution power networks,industrial installations, in buildings and operation stations .These cables can be fixed on cable trays, indoors, in cable ducts, outdoors and underground .

STANDARDS

IEC 60228 Conductors of insulated cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from

1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV(Um=1.2kV) and

3 kV(Um=3.6kV)

Note: We also can produce based on other international standards, such as BS , AS/NZS, VDE and other standards.

CHAIRCTERITICS

● Maximum conductor temperature in normal operation: 70˚C.

● Short Circuit Temperature ( 5 seconds maximum duration ): Shall not exceed 160˚C when the cables conductor section not exceed300sq.mm, not exceed 140˚C when the cables conductor section more than 300sq.mm.

●Good electrical and mechanical properties.

● Minimum bending radius:

| Items | Single-core Cables |  | Three-core Cables |  |
| --- | --- | --- | --- | --- |
|  | Unarmoured | Armoured | Unarmoured | Armoured |
| Min. bending radius during installation | 20D | 15D | 15D | 12D |
| Min. bending radius close to connection box and termination (bending radius should be controlled carefully, if the molding guide plate is used) | 15D | 12D | 12D | 10D |

Note:D is overall diameter of cable.

TYPE & SPECIFICATION

| Type |  | Designation |
| --- | --- | --- |
| NYY(VV) | NAYY(VLV) | Cu or Al core PVC insulated PVC sheathed power cable |
| NY2Y(VY) | NAY2Y(VLY) | Cu or Al core PVC insulated PE sheathed power cable |
| NYBY(VV62) | NAYBY(VLV62) | Cu or Al core PVC insulated non-magnetic metal tape armoured PVC sheathed power cable |
| NYB2Y(VY63) | NAYB2Y(VLY63) | Cu or Al core PVC insulated non-magnetic metal tape armoured PE sheathed power cable |
| NYRY(VV72) | NAYRY(VLV72) | Cu or Al core PVC insulated non-magnetic wire armoured PVC sheathed power cable |
| NYR2Y(VY73) | NAYR2Y(VLY73) | Cu or Al core PVC insulated non-magnetic wire armoured PE sheathed power cable |
| NYBY(VV22) | NAYBY(VLV22) | Cu or Al core PVC insulated steel tape armoured PVC sheathed power cable |
| NYB2Y(VY23) | NAYB2Y(VLY23) | Cu or Al core PVC insulated steel tape armoured PE sheathed power cable |
| NYRY(VV32) | NAYRY(VLV32) | Cu or Al core PVC insulated steel wire armoured PVC sheathed power cable |
| NYR2Y(VY33) | NAYR2Y(VLY33) | Cu or Al core PVC insulated steel wire armoured PE sheathed power cable |

CONSTRUCTION STRUCTION

Conductors

The conductors shall be either of Class 1 or Class 2 of plain or metal-coated annealed copper or of plain aluminium or aluminium alloy, or of Class 5 of plain or metal-coated copper in accordance with IEC 60228.

Insulation

This will be an extruded layer of PVC applied over conductor .

Laying-up

In case of multi-core cables, the multi-core are laid up with non-hygroscopic fillers at interstices and a binder tape is applied with an overlap. These binder tapes can be of non-hygroscopic material.

Inner sheath

Extruded layer of PVC or PE is applied over the laid up cores for armoured cables. PVC is normally of grade ST1 and PE of grade ST3 as per IEC 60502 -1.

Armour

Armour shall be as per IEC 60502-1 of the following types:

- Round Wire Armour

- Double Tape Armour

Armour material shall be Galvanized steel for three core cables and Non-magnetic material (Non-magnetic steel or Aluminium etc.) for single core cables. Armour of other material as per IEC 60502-1 can be provided upon request.

Outer Sheath

Outer sheath material can be either PVC, LDPE, MDPE, HDPE or LSZH.Other colors may be provided to suit a range of installation considerations such as the effect of UV radiations.When the cable is required to ant-termite / anti-vermin, a special additive is added to the sheathing compound.

Flame-retardant (optional)

In the event of a fire, there is a risk of the fire spreading through cables. To prevent this from happening, cables can be provided with sheaths made of a flame retardant material.

VV (NYY)  Single Core  0.6/1kV

CU/PVC/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Copper,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 1×1.5 | 1 | 0.8 | 1.4 | 5.8 | 49 | 12.1 |
| 1×2.5 | 1 | 0.8 | 1.4 | 6.2 | 61 | 7.41 |
| 1×4 | 1 | 1.0 | 1.4 | 7.0 | 85 | 4.61 |
| 1×6 | 1 | 1.0 | 1.4 | 7.5 | 108 | 3.08 |
| 1×10 | 6 | 1.0 | 1.4 | 8.8 | 157 | 1.83 |
| 1×16 | 6 | 1.0 | 1.4 | 9.6 | 218 | 1.15 |
| 1×25 | 6 | 1.2 | 1.4 | 11.2 | 320 | 0.727 |
| 1×35 | 6 | 1.2 | 1.4 | 12.2 | 416 | 0.524 |
| 1×50 | 6 | 1.4 | 1.4 | 13.9 | 551 | 0.387 |
| 1×70 | 12 | 1.4 | 1.5 | 15.6 | 761 | 0.268 |
| 1×95 | 15 | 1.6 | 1.5 | 17.8 | 1030 | 0.193 |
| 1×120 | 18 | 1.6 | 1.6 | 19.4 | 1274 | 0.153 |
| 1×150 | 18 | 1.8 | 1.6 | 21.1 | 1554 | 0.124 |
| 1×185 | 30 | 2.0 | 1.7 | 23.4 | 1943 | 0.0991 |
| 1×240 | 34 | 2.2 | 1.8 | 26.3 | 2508 | 0.0754 |
| 1×300 | 34 | 2.4 | 1.9 | 29.1 | 3123 | 0.0601 |
| 1×400 | 53 | 2.6 | 2.0 | 32.4 | 3981 | 0.0470 |
| 1×500 | 53 | 2.8 | 2.1 | 36.1 | 5014 | 0.0366 |
| 1×630 | 53 | 2.8 | 2.2 | 40.0 | 6392 | 0.0283 |

VV (NYY)  Multi- Core  0.6/1kV

CU/PVC/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion. .

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.8 | 1.8 | 9.8 | 117 | 12.1 |
| 2×2.5 | 1 | 0.8 | 1.8 | 10.6 | 145 | 7.41 |
| 2×4 | 1 | 1.0 | 1.8 | 12.4 | 203 | 4.61 |
| 2×6 | 1 | 1.0 | 1.8 | 13.4 | 257 | 3.08 |
| 2×10 | 6 | 1.0 | 1.8 | 15.9 | 373 | 1.83 |
| 2×16 | 6 | 1.0 | 1.8 | 17.5 | 508 | 1.15 |
| 2×25 | 6 | 1.2 | 1.8 | 20.7 | 740 | 0.727 |
| 2×35 | 6 | 1.2 | 1.8 | 22.7 | 954 | 0.524 |
| 2×50 | 6 | 1.4 | 1.8 | 26.1 | 1264 | 0.387 |
| 2×70 | 12 | 1.4 | 1.9 | 29.6 | 1701 | 0.268 |
| 2×95 | 15 | 1.6 | 2.0 | 34.2 | 2311 | 0.193 |
| 2×120 | 18 | 1.6 | 2.1 | 37.2 | 2841 | 0.153 |
| 2×150 | 18 | 1.8 | 2.2 | 41.2 | 3486 | 0.124 |
| 2×185 | 30 | 2.0 | 2.4 | 45.6 | 4351 | 0.0991 |
| 2×240 | 34 | 2.2 | 2.6 | 51.4 | 5613 | 0.0754 |
| 2×300 | 34 | 2.4 | 2.7 | 56.8 | 6961 | 0.0601 |
| 2×400 | 53 | 2.6 | 3.0 | 63.8 | 8896 | 0.0470 |
| 3×1.5 | 1 | 0.8 | 1.8 | 10.3 | 141 | 12.1 |
| 3×2.5 | 1 | 0.8 | 1.8 | 11.2 | 179 | 7.41 |
| 3×4 | 1 | 1.0 | 1.8 | 13.0 | 256 | 4.61 |
| 3×6 | 1 | 1.0 | 1.8 | 14.1 | 330 | 3.08 |
| 3×10 | 6 | 1.0 | 1.8 | 16.9 | 487 | 1.83 |
| 3×16 | 6 | 1.0 | 1.8 | 18.6 | 679 | 1.15 |
| 3×25 | 6 | 1.2 | 1.8 | 22.0 | 1000 | 0.727 |
| 3X35 | 6 | 1.2 | 1.8 | 24.2 | 1304 | 0.524 |
| 3×50 | 6 | 1.4 | 1.8 | 27.9 | 1735 | 0.387 |
| 3×70 | 12 | 1.4 | 2.0 | 31.8 | 2383 | 0.268 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×95 | 15 | 1.6 | 2.1 | 36.8 | 3248 | 0.193 |
| 3×120 | 18 | 1.6 | 2.2 | 40.0 | 4005 | 0.153 |
| 3×150 | 18 | 1.8 | 2.3 | 44.3 | 4919 | 0.124 |
| 3×185 | 30 | 2.0 | 2.5 | 49.0 | 6147 | 0.0991 |
| 3×240 | 34 | 2.2 | 2.7 | 55.2 | 7942 | 0.0754 |
| 3×300 | 34 | 2.4 | 2.9 | 61.3 | 9896 | 0.0601 |
| 3×400 | 53 | 2.6 | 3.1 | 68.6 | 12621 | 0.0470 |
| 4×1.5 | 1 | 0.8 | 1.8 | 11.1 | 170 | 12.1 |
| 4×2.5 | 1 | 0.8 | 1.8 | 12.0 | 218 | 7.41 |
| 4×4 | 1 | 1.0 | 1.8 | 14.1 | 317 | 4.61 |
| 4×6 | 1 | 1.0 | 1.8 | 15.4 | 413 | 3.08 |
| 4×10 | 6 | 1.0 | 1.8 | 18.4 | 615 | 1.83 |
| 4×16 | 6 | 1.0 | 1.8 | 20.4 | 866 | 1.15 |
| 4×25 | 6 | 1.2 | 1.8 | 24.2 | 1284 | 0.727 |
| 4×35 | 6 | 1.2 | 1.8 | 26.6 | 1682 | 0.524 |
| 4×50 | 6 | 1.4 | 1.9 | 31.3 | 2268 | 0.387 |
| 4×70 | 12 | 1.4 | 2.1 | 35.3 | 3110 | 0.268 |
| 4×95 | 15 | 1.6 | 2.2 | 40.8 | 4245 | 0.193 |
| 4×120 | 18 | 1.6 | 2.3 | 44.4 | 5239 | 0.153 |
| 4×150 | 18 | 1.8 | 2.5 | 49.4 | 6460 | 0.124 |
| 4×185 | 30 | 2.0 | 2.7 | 54.6 | 8072 | 0.0991 |
| 4×240 | 34 | 2.2 | 2.9 | 61.6 | 10431 | 0.0754 |
| 4×300 | 34 | 2.4 | 3.1 | 68.3 | 12998 | 0.0601 |
| 4×400 | 53 | 2.6 | 3.4 | 76.6 | 16617 | 0.0470 |
| 5×1.5 | 1 | 0.8 | 1.8 | 11.9 | 200 | 12.1 |
| 5×2.5 | 1 | 0.8 | 1.8 | 13.0 | 259 | 7.41 |
| 5×4 | 1 | 1.0 | 1.8 | 15.3 | 381 | 4.61 |
| 5×6 | 1 | 1.0 | 1.8 | 16.7 | 499 | 3.08 |
| 5×10 | 6 | 1.0 | 1.8 | 20.1 | 749 | 1.83 |
| 5×16 | 6 | 1.0 | 1.8 | 22.3 | 1060 | 1.15 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 5×25 | 6 | 1.2 | 1.8 | 26.6 | 1577 | 0.727 |
| 5×35 | 6 | 1.2 | 1.9 | 29.8 | 2093 | 0.524 |
| 5×50 | 6 | 1.4 | 2.0 | 34.6 | 2811 | 0.387 |
| 5×70 | 12 | 1.4 | 2.2 | 39.0 | 3857 | 0.268 |
| 5×95 | 15 | 1.6 | 2.4 | 45.4 | 5288 | 0.193 |
| 5×120 | 18 | 1.6 | 2.5 | 49.3 | 6526 | 0.153 |
| 5×150 | 18 | 1.8 | 2.7 | 54.9 | 8044 | 0.124 |
| 5×185 | 30 | 2.0 | 2.9 | 60.7 | 10048 | 0.0991 |
| 5×240 | 34 | 2.2 | 3.1 | 68.4 | 12983 | 0.0754 |
| 5×300 | 34 | 2.4 | 3.3 | 75.8 | 16177 | 0.0601 |
| 5×400 | 53 | 2.6 | 3.7 | 85.2 | 20715 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.8/0.8 | 1.8 | 11.8 | 206 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 1.8 | 13.6 | 292 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 1.8 | 15.1 | 389 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 1.8 | 17.7 | 564 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 1.8 | 19.9 | 803 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 1.8 | 23.3 | 1177 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 1.8 | 25.1 | 1474 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 1.9 | 29.6 | 2023 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 33.2 | 2741 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 2.2 | 38.6 | 3750 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.6/1.4 | 2.3 | 42.2 | 4710 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.8/1.4 | 2.4 | 45.9 | 5606 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 2.6 | 51.2 | 7104 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 2.2/1.6 | 2.8 | 57.4 | 9120 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 2.4/1.8 | 3.0 | 63.7 | 11347 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 3.2 | 71.1 | 14431 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.8/0.8 | 1.8 | 12.5 | 235 | 7.41/12.1 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 1.8 | 14.4 | 331 | 4.61/7.41 |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 1.8 | 16.1 | 451 | 3.08/4.61 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 1.8 | 18.7 | 647 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 1.8 | 21.4 | 935 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 1.8 | 24.9 | 1366 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 1.8 | 26.5 | 1660 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 1.9 | 31.5 | 2310 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 2.1 | 35.4 | 3138 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 2.2 | 41.0 | 4266 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.6/1.4 | 2.4 | 45.3 | 5451 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.8/1.4 | 2.5 | 48.5 | 6341 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 2.7 | 54.5 | 8118 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 2.2/1.6 | 2.9 | 60.8 | 10371 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 2.4/1.8 | 3.1 | 67.5 | 12889 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 3.3 | 75.2 | 16355 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.8/0.8 | 1.8 | 12.8 | 247 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 1.8 | 14.9 | 356 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 1.8 | 16.4 | 475 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 1.8 | 19.4 | 698 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 1.8 | 21.8 | 997 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 1.8 | 25.7 | 1471 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 1.8 | 27.9 | 1865 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 33.1 | 2567 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 2.1 | 37.1 | 3487 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 2.3 | 43.2 | 4775 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.6/1.4 | 2.4 | 47.2 | 5976 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.8/1.4 | 2.6 | 51.7 | 7188 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 2.8 | 57.6 | 9079 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 2.2/1.6 | 3.0 | 64.6 | 11671 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 2.4/1.8 | 3.2 | 71.6 | 14525 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 3.5 | 80.2 | 18523 | 0.0470/0.0991 |

VLV (NAYY)  Single Core  0.6/1kV

AL/PVC/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 1×2.5 | 1 | 0.8 | 1.4 | 6.2 | 46 | 12.1 |
| 1×4 | 1 | 1.0 | 1.4 | 7.0 | 61 | 7.41 |
| 1×6 | 1 | 1.0 | 1.4 | 7.5 | 73 | 4.61 |
| 1×10 | 6 | 1.0 | 1.4 | 8.8 | 93 | 3.08 |
| 1×16 | 6 | 1.0 | 1.4 | 9.6 | 120 | 1.91 |
| 1×25 | 6 | 1.2 | 1.4 | 11.2 | 167 | 1.20 |
| 1×35 | 6 | 1.2 | 1.4 | 12.2 | 205 | 0.868 |
| 1×50 | 6 | 1.4 | 1.4 | 13.9 | 263 | 0.641 |
| 1×70 | 12 | 1.4 | 1.5 | 15.6 | 340 | 0.443 |
| 1×95 | 15 | 1.6 | 1.5 | 17.8 | 456 | 0.320 |
| 1×120 | 15 | 1.6 | 1.6 | 19.4 | 537 | 0.253 |
| 1×150 | 15 | 1.8 | 1.6 | 21.1 | 660 | 0.206 |
| 1×185 | 30 | 2.0 | 1.7 | 23.4 | 814 | 0.164 |
| 1×240 | 30 | 2.2 | 1.8 | 26.3 | 1043 | 0.125 |
| 1×300 | 30 | 2.4 | 1.9 | 29.1 | 1284 | 0.100 |
| 1×400 | 53 | 2.6 | 2.0 | 32.4 | 1612 | 0.0778 |
| 1×500 | 53 | 2.8 | 2.1 | 36.1 | 2007 | 0.0605 |
| 1×630 | 53 | 2.8 | 2.2 | 40.0 | 2488 | 0.0469 |

VLV (NAYY)  Multi- Core  0.6/1kV

AL/PVC/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be fixed on cable trays, within conduits or fixed to walls.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler: Non-hygroscopic material

- Binder: Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.8 | 1.8 | 10.6 | 116 | 12.1 |
| 2×4 | 1 | 1.0 | 1.8 | 12.4 | 156 | 7.41 |
| 2×6 | 1 | 1.0 | 1.8 | 13.4 | 186 | 4.61 |
| 2×10 | 6 | 1.0 | 1.8 | 15.9 | 240 | 3.08 |
| 2×16 | 6 | 1.0 | 1.8 | 17.5 | 310 | 1.91 |
| 2×25 | 6 | 1.2 | 1.8 | 20.7 | 433 | 1.20 |
| 2×35 | 6 | 1.2 | 1.8 | 22.7 | 529 | 0.868 |
| 2×50 | 6 | 1.4 | 1.8 | 26.1 | 679 | 0.641 |
| 2×70 | 12 | 1.4 | 1.9 | 29.6 | 869 | 0.443 |
| 2×95 | 15 | 1.6 | 2.0 | 34.2 | 1157 | 0.320 |
| 2×120 | 15 | 1.6 | 2.1 | 37.2 | 1369 | 0.253 |
| 2×150 | 15 | 1.8 | 2.2 | 41.2 | 1682 | 0.206 |
| 2×185 | 30 | 2.0 | 2.4 | 45.6 | 2078 | 0.164 |
| 2×240 | 30 | 2.2 | 2.6 | 51.4 | 2664 | 0.125 |
| 2×300 | 30 | 2.4 | 2.7 | 56.8 | 3257 | 0.100 |
| 2×400 | 53 | 2.6 | 3.0 | 63.8 | 4116 | 0.0778 |
| 3×2.5 | 1 | 0.8 | 1.8 | 11.2 | 135 | 12.1 |
| 3×4 | 1 | 1.0 | 1.8 | 13.0 | 185 | 7.41 |
| 3×6 | 1 | 1.0 | 1.8 | 14.1 | 223 | 4.61 |
| 3×10 | 6 | 1.0 | 1.8 | 16.9 | 292 | 3.08 |
| 3×16 | 6 | 1.0 | 1.8 | 18.6 | 382 | 1.91 |
| 3×25 | 6 | 1.2 | 1.8 | 22.0 | 540 | 1.20 |
| 3X35 | 6 | 1.2 | 1.8 | 24.2 | 666 | 0.868 |
| 3×50 | 6 | 1.4 | 1.8 | 27.9 | 861 | 0.641 |
| 3×70 | 12 | 1.4 | 2.0 | 31.8 | 1135 | 0.443 |
| 3×95 | 15 | 1.6 | 2.1 | 36.8 | 1517 | 0.320 |
| 3×120 | 15 | 1.6 | 2.2 | 40.0 | 1803 | 0.253 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×150 | 15 | 1.8 | 2.3 | 44.3 | 2213 | 0.206 |
| 3×185 | 30 | 2.0 | 2.5 | 49.0 | 2739 | 0.164 |
| 3×240 | 30 | 2.2 | 2.7 | 55.2 | 3519 | 0.125 |
| 3×300 | 30 | 2.4 | 2.9 | 61.3 | 4343 | 0.100 |
| 3×400 | 53 | 2.6 | 3.1 | 68.6 | 5458 | 0.0778 |
| 4×2.5 | 1 | 0.8 | 1.8 | 12.0 | 160 | 12.1 |
| 4×4 | 1 | 1.0 | 1.8 | 14.1 | 221 | 7.41 |
| 4×6 | 1 | 1.0 | 1.8 | 15.4 | 269 | 4.61 |
| 4×10 | 6 | 1.0 | 1.8 | 18.4 | 356 | 3.08 |
| 4×16 | 6 | 1.0 | 1.8 | 20.4 | 470 | 1.91 |
| 4×25 | 6 | 1.2 | 1.8 | 24.2 | 671 | 1.20 |
| 4×35 | 6 | 1.2 | 1.8 | 26.6 | 832 | 0.868 |
| 4×50 | 6 | 1.4 | 1.9 | 31.3 | 1104 | 0.641 |
| 4×70 | 12 | 1.4 | 2.1 | 35.3 | 1446 | 0.443 |
| 4×95 | 15 | 1.6 | 2.2 | 40.8 | 1937 | 0.320 |
| 4×120 | 15 | 1.6 | 2.3 | 44.4 | 2304 | 0.253 |
| 4×150 | 15 | 1.8 | 2.5 | 49.4 | 2852 | 0.206 |
| 4×185 | 30 | 2.0 | 2.7 | 54.6 | 3528 | 0.164 |
| 4×240 | 30 | 2.2 | 2.9 | 61.6 | 4533 | 0.125 |
| 4×300 | 30 | 2.4 | 3.1 | 68.3 | 5595 | 0.100 |
| 4×400 | 53 | 2.6 | 3.4 | 76.6 | 7068 | 0.0778 |
| 5×2.5 | 1 | 0.8 | 1.8 | 13.0 | 186 | 12.1 |
| 5×4 | 1 | 1.0 | 1.8 | 15.3 | 261 | 7.41 |
| 5×6 | 1 | 1.0 | 1.8 | 16.7 | 319 | 4.61 |
| 5×10 | 6 | 1.0 | 1.8 | 20.1 | 424 | 3.08 |
| 5×16 | 6 | 1.0 | 1.8 | 22.3 | 564 | 1.91 |
| 5×25 | 6 | 1.2 | 1.8 | 26.6 | 812 | 1.20 |
| 5×35 | 6 | 1.2 | 1.9 | 29.8 | 1031 | 0.868 |
| 5×50 | 6 | 1.4 | 2.0 | 34.6 | 1356 | 0.641 |
| 5×70 | 12 | 1.4 | 2.2 | 39.0 | 1776 | 0.443 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 5×95 | 15 | 1.6 | 2.4 | 45.4 | 2403 | 0.320 |
| 5×120 | 15 | 1.6 | 2.5 | 49.3 | 2858 | 0.253 |
| 5×150 | 15 | 1.8 | 2.7 | 54.9 | 3534 | 0.206 |
| 5×185 | 30 | 2.0 | 2.9 | 60.7 | 4368 | 0.164 |
| 5×240 | 30 | 2.2 | 3.1 | 68.4 | 5611 | 0.125 |
| 5×300 | 30 | 2.4 | 3.3 | 75.8 | 6924 | 0.100 |
| 5×400 | 53 | 2.6 | 3.7 | 85.2 | 8780 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 1.8 | 13.6 | 206 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 1.8 | 15.1 | 257 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 1.8 | 17.7 | 333 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 1.8 | 19.9 | 441 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 1.8 | 23.3 | 619 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 1.8 | 25.1 | 738 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 1.9 | 29.6 | 989 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 33.2 | 1281 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 2.2 | 38.6 | 1728 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.6/1.4 | 2.3 | 42.2 | 2093 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.8/1.4 | 2.4 | 45.9 | 2484 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 2.6 | 51.2 | 3119 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 2.2/1.6 | 2.8 | 57.4 | 3962 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 2.4/1.8 | 3.0 | 63.7 | 4894 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 3.2 | 71.1 | 6135 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 1.8 | 14.4 | 230 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 1.8 | 16.1 | 295 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 1.8 | 18.7 | 381 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 1.8 | 21.4 | 507 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 1.8 | 24.9 | 710 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 1.8 | 26.5 | 825 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 1.9 | 31.5 | 1132 | 0.641/1.20 |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 2.1 | 35.4 | 1464 | 0.443/0.868 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | kg/km | Ω/km |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 2.2 | 41.0 | 1952 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.6/1.4 | 2.4 | 45.3 | 2419 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.8/1.4 | 2.5 | 48.5 | 2803 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 2.7 | 54.5 | 3556 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 2.2/1.6 | 2.9 | 60.8 | 4479 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 2.4/1.8 | 3.1 | 67.5 | 5534 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 3.3 | 75.2 | 6924 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 1.8 | 14.9 | 245 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 1.8 | 16.4 | 307 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 1.8 | 19.4 | 403 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 1.8 | 21.8 | 535 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 1.8 | 25.7 | 760 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 1.8 | 27.9 | 917 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 33.1 | 1250 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 2.1 | 37.1 | 1611 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 2.3 | 43.2 | 2175 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.6/1.4 | 2.4 | 47.2 | 2626 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.8/1.4 | 2.6 | 51.7 | 3164 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 2.8 | 57.6 | 3957 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 2.2/1.6 | 3.0 | 64.6 | 5039 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 2.4/1.8 | 3.2 | 71.6 | 6221 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 3.5 | 80.2 | 7841 | 0.0778/0.164 |

VV62 (NYBY)  Single Core  0.6/1kV

CU/PVC/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Inter sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magnetic steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 1.0 | 0.2 | 1.4 | 11.6 | 269 | 1.83 |
| 1×16 | 6 | 1.0 | 0.2 | 1.4 | 12.4 | 340 | 1.15 |
| 1×25 | 6 | 1.2 | 0.2 | 1.4 | 14.0 | 461 | 0.727 |
| 1×35 | 6 | 1.2 | 0.2 | 1.4 | 15.0 | 569 | 0.524 |
| 1×50 | 6 | 1.4 | 0.2 | 1.5 | 16.9 | 732 | 0.387 |
| 1×70 | 12 | 1.4 | 0.2 | 1.5 | 18.4 | 953 | 0.268 |
| 1×95 | 15 | 1.6 | 0.2 | 1.6 | 20.8 | 1259 | 0.193 |
| 1×120 | 18 | 1.6 | 0.2 | 1.6 | 22.2 | 1512 | 0.153 |
| 1×150 | 18 | 1.8 | 0.2 | 1.7 | 24.3 | 1829 | 0.124 |
| 1×185 | 30 | 2.0 | 0.2 | 1.8 | 26.5 | 2242 | 0.0991 |
| 1×240 | 34 | 2.2 | 0.2 | 1.9 | 29.4 | 2843 | 0.0754 |
| 1×300 | 34 | 2.4 | 0.2 | 1.9 | 32.0 | 3478 | 0.0601 |
| 1×400 | 53 | 2.6 | 0.2 | 2.1 | 36.0 | 4432 | 0.0470 |
| 1×500 | 53 | 2.8 | 0.5 | 2.2 | 40.7 | 5889 | 0.0366 |
| 1×630 | 53 | 2.8 | 0.5 | 2.3 | 44.6 | 7359 | 0.0283 |

VLV62 (NAYBY)  Single Core  0.6/1kV

AL/PVC/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Inner sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magnetic steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 1.0 | 0.2 | 1.4 | 11.6 | 203 | 3.08 |
| 1×16 | 6 | 1.0 | 0.2 | 1.4 | 12.4 | 241 | 1.91 |
| 1×25 | 6 | 1.2 | 0.2 | 1.4 | 14.0 | 308 | 1.20 |
| 1×35 | 6 | 1.2 | 0.2 | 1.4 | 15.0 | 358 | 0.868 |
| 1×50 | 6 | 1.4 | 0.2 | 1.5 | 16.9 | 441 | 0.641 |
| 1×70 | 12 | 1.4 | 0.2 | 1.5 | 18.4 | 539 | 0.443 |
| 1×95 | 15 | 1.6 | 0.2 | 1.6 | 20.8 | 685 | 0.320 |
| 1×120 | 15 | 1.6 | 0.2 | 1.6 | 22.2 | 781 | 0.253 |
| 1×150 | 15 | 1.8 | 0.2 | 1.7 | 24.3 | 932 | 0.206 |
| 1×185 | 30 | 2.0 | 0.2 | 1.8 | 26.5 | 1112 | 0.164 |
| 1×240 | 30 | 2.2 | 0.2 | 1.9 | 29.4 | 1376 | 0.125 |
| 1×300 | 30 | 2.4 | 0.2 | 1.9 | 32.0 | 1636 | 0.100 |
| 1×400 | 53 | 2.6 | 0.2 | 2.1 | 36.0 | 2056 | 0.0778 |
| 1×500 | 53 | 2.8 | 0.5 | 2.2 | 40.7 | 2882 | 0.0605 |
| 1×630 | 53 | 2.8 | 0.5 | 2.3 | 44.6 | 3454 | 0.0469 |

VV22 (NYBY)  Multi-Core  0.6/1kV

CU/PVC/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.8 | 0.2 | 1.8 | 12.6 | 236 | 12.1 |
| 2×2.5 | 1 | 0.8 | 0.2 | 1.8 | 13.4 | 274 | 7.41 |
| 2×4 | 1 | 1.0 | 0.2 | 1.8 | 15.2 | 354 | 4.61 |
| 2×6 | 1 | 1.0 | 0.2 | 1.8 | 16.2 | 419 | 3.08 |
| 2×10 | 6 | 1.0 | 0.2 | 1.8 | 18.7 | 566 | 1.83 |
| 2×16 | 6 | 1.0 | 0.2 | 1.8 | 20.3 | 721 | 1.15 |
| 2×25 | 6 | 1.2 | 0.2 | 1.8 | 23.5 | 991 | 0.727 |
| 2×35 | 6 | 1.2 | 0.2 | 1.8 | 25.5 | 1229 | 0.524 |
| 2×50 | 6 | 1.4 | 0.2 | 1.8 | 28.9 | 1580 | 0.387 |
| 2×70 | 12 | 1.4 | 0.2 | 1.9 | 32.8 | 2094 | 0.268 |
| 2×95 | 15 | 1.6 | 0.5 | 2.1 | 38.8 | 3144 | 0.193 |
| 2×120 | 18 | 1.6 | 0.5 | 2.2 | 41.8 | 3743 | 0.153 |
| 2×150 | 18 | 1.8 | 0.5 | 2.4 | 46.4 | 4545 | 0.124 |
| 2×185 | 30 | 2.0 | 0.5 | 2.5 | 50.6 | 5493 | 0.0991 |
| 2×240 | 34 | 2.2 | 0.5 | 2.7 | 56.4 | 6894 | 0.0754 |
| 2×300 | 34 | 2.4 | 0.5 | 2.9 | 62.4 | 8467 | 0.0601 |
| 2×400 | 53 | 2.6 | 0.5 | 3.1 | 69.2 | 10547 | 0.0470 |
| 3×1.5 | 1 | 0.8 | 0.2 | 1.8 | 13.1 | 266 | 12.1 |
| 3×2.5 | 1 | 0.8 | 0.2 | 1.8 | 14.0 | 314 | 7.41 |
| 3×4 | 1 | 1.0 | 0.2 | 1.8 | 15.8 | 415 | 4.61 |
| 3×6 | 1 | 1.0 | 0.2 | 1.8 | 16.9 | 502 | 3.08 |
| 3×10 | 6 | 1.0 | 0.2 | 1.8 | 19.7 | 692 | 1.83 |
| 3×16 | 6 | 1.0 | 0.2 | 1.8 | 21.4 | 905 | 1.15 |
| 3×25 | 6 | 1.2 | 0.2 | 1.8 | 24.8 | 1267 | 0.727 |
| 3X35 | 6 | 1.2 | 0.2 | 1.8 | 27.0 | 1597 | 0.524 |
| 3×50 | 6 | 1.4 | 0.2 | 1.9 | 30.9 | 2087 | 0.387 |
| 3×70 | 12 | 1.4 | 0.2 | 2.0 | 35.0 | 2804 | 0.268 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×95 | 15 | 1.6 | 0.5 | 2.2 | 41.4 | 4140 | 0.193 |
| 3×120 | 18 | 1.6 | 0.5 | 2.3 | 44.6 | 4971 | 0.153 |
| 3×150 | 18 | 1.8 | 0.5 | 2.5 | 49.5 | 6054 | 0.124 |
| 3×185 | 30 | 2.0 | 0.5 | 2.6 | 54.0 | 7371 | 0.0991 |
| 3×240 | 34 | 2.2 | 0.5 | 2.8 | 60.6 | 9380 | 0.0754 |
| 3×300 | 34 | 2.4 | 0.5 | 3.0 | 66.7 | 11484 | 0.0601 |
| 3×400 | 53 | 2.6 | 0.5 | 3.3 | 74.6 | 14504 | 0.0470 |
| 4×1.5 | 1 | 0.8 | 0.2 | 1.8 | 13.9 | 304 | 12.1 |
| 4×2.5 | 1 | 0.8 | 0.2 | 1.8 | 14.8 | 364 | 7.41 |
| 4×4 | 1 | 1.0 | 0.2 | 1.8 | 16.9 | 489 | 4.61 |
| 4×6 | 1 | 1.0 | 0.2 | 1.8 | 18.2 | 600 | 3.08 |
| 4×10 | 6 | 1.0 | 0.2 | 1.8 | 21.2 | 839 | 1.83 |
| 4×16 | 6 | 1.0 | 0.2 | 1.8 | 23.2 | 1113 | 1.15 |
| 4×25 | 6 | 1.2 | 0.2 | 1.8 | 27.0 | 1578 | 0.727 |
| 4×35 | 6 | 1.2 | 0.2 | 1.9 | 29.6 | 2019 | 0.524 |
| 4×50 | 6 | 1.4 | 0.2 | 2.0 | 34.7 | 2698 | 0.387 |
| 4×70 | 12 | 1.4 | 0.5 | 2.2 | 39.9 | 3966 | 0.268 |
| 4×95 | 15 | 1.6 | 0.5 | 2.4 | 46.0 | 5295 | 0.193 |
| 4×120 | 18 | 1.6 | 0.5 | 2.5 | 49.6 | 6377 | 0.153 |
| 4×150 | 18 | 1.8 | 0.5 | 2.6 | 54.4 | 7694 | 0.124 |
| 4×185 | 30 | 2.0 | 0.5 | 2.8 | 60.0 | 9495 | 0.0991 |
| 4×240 | 34 | 2.2 | 0.5 | 3.0 | 67.0 | 12027 | 0.0754 |
| 4×300 | 34 | 2.4 | 0.5 | 3.2 | 74.1 | 14840 | 0.0601 |
| 4×400 | 53 | 2.6 | 0.5 | 3.5 | 82.4 | 18673 | 0.0470 |
| 5×1.5 | 1 | 0.8 | 0.2 | 1.8 | 14.7 | 344 | 12.1 |
| 5×2.5 | 1 | 0.8 | 0.2 | 1.8 | 15.8 | 417 | 7.41 |
| 5×4 | 1 | 1.0 | 0.2 | 1.8 | 18.1 | 567 | 4.61 |
| 5×6 | 1 | 1.0 | 0.2 | 1.8 | 19.5 | 702 | 3.08 |
| 5×10 | 6 | 1.0 | 0.2 | 1.8 | 22.9 | 992 | 1.83 |
| 5×16 | 6 | 1.0 | 0.2 | 1.8 | 25.1 | 1330 | 1.15 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×25 | 6 | 1.2 | 0.2 | 1.9 | 29.6 | 1913 | 0.727 |
| 5×35 | 6 | 1.2 | 0.2 | 1.9 | 33.0 | 2489 | 0.524 |
| 5×50 | 6 | 1.4 | 0.5 | 2.2 | 39.4 | 3670 | 0.387 |
| 5×70 | 12 | 1.4 | 0.5 | 2.3 | 43.6 | 4799 | 0.268 |
| 5×95 | 15 | 1.6 | 0.5 | 2.5 | 50.4 | 6424 | 0.193 |
| 5×120 | 18 | 1.6 | 0.5 | 2.6 | 54.3 | 7758 | 0.153 |
| 5×150 | 18 | 1.8 | 0.5 | 2.8 | 60.3 | 9472 | 0.124 |
| 5×185 | 30 | 2.0 | 0.5 | 3.0 | 66.1 | 11621 | 0.0991 |
| 5×240 | 34 | 2.2 | 0.5 | 3.2 | 74.2 | 14827 | 0.0754 |
| 5×300 | 34 | 2.4 | 0.5 | 3.5 | 81.8 | 18251 | 0.0601 |
| 5×400 | 53 | 2.6 | 0.8 | 3.8 | 92.2 | 23887 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.8/0.8 | 0.2 | 1.8 | 14.6 | 349 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 16.4 | 457 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 17.9 | 572 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 20.5 | 778 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 22.7 | 1044 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 26.1 | 1459 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 27.9 | 1778 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 0.2 | 1.9 | 32.8 | 2416 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 0.2 | 2.1 | 36.6 | 3196 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 0.5 | 2.3 | 43.2 | 4683 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.6/1.4 | 0.5 | 2.4 | 47.2 | 5771 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.8/1.4 | 0.5 | 2.5 | 50.9 | 6755 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 0.5 | 2.7 | 56.2 | 8381 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 2.2/1.6 | 0.5 | 2.9 | 62.8 | 10611 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 2.4/1.8 | 0.5 | 3.1 | 69.1 | 12994 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 0.5 | 3.3 | 76.9 | 16345 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.8/0.8 | 0.2 | 1.8 | 15.3 | 388 | 7.41/12.1 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 17.2 | 506 | 4.61/7.41 |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 18.9 | 647 | 3.08/4.61 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 21.5 | 875 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 24.2 | 1194 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 27.7 | 1668 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 0.2 | 1.9 | 29.5 | 1994 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 0.2 | 2.0 | 34.9 | 2743 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 0.5 | 2.2 | 40.0 | 3996 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 0.5 | 2.4 | 46.2 | 5320 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.6/1.4 | 0.5 | 2.5 | 50.3 | 6585 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.8/1.4 | 0.5 | 2.6 | 53.5 | 7554 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 0.5 | 2.8 | 59.9 | 9538 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 2.2/1.6 | 0.5 | 3.0 | 66.2 | 11948 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 2.4/1.8 | 0.5 | 3.2 | 72.9 | 14632 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 0.5 | 3.5 | 81.2 | 18414 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.8/0.8 | 0.2 | 1.8 | 15.6 | 402 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 17.7 | 536 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 19.2 | 674 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 22.2 | 933 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 24.6 | 1262 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 28.5 | 1783 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.9 | 30.9 | 2217 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 0.2 | 2.1 | 36.5 | 3021 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 0.5 | 2.3 | 41.9 | 4405 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 0.5 | 2.4 | 48.2 | 5859 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.6/1.4 | 0.5 | 2.6 | 52.4 | 7181 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.8/1.4 | 0.5 | 2.7 | 57.1 | 8537 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 0.5 | 2.9 | 63.0 | 10575 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 2.2/1.6 | 0.5 | 3.1 | 70.0 | 13342 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 2.4/1.8 | 0.5 | 3.3 | 77.4 | 16455 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 0.8 | 3.7 | 87.4 | 21557 | 0.0470/0.0991 |

VLV22 (NAYBY)  Multi-Core  0.6/1kV

AL/PVC/STA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. These cables can be laying indoor, tunnel and underground. Able to bear external mechanical force, but unable to bear large pulling force.

CONSTRUCTION

- Conductor : Aluminum ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel tape

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYBY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.8 | 0.2 | 1.8 | 13.4 | 246 | 12.1 |
| 2×4 | 1 | 1.0 | 0.2 | 1.8 | 15.2 | 306 | 7.41 |
| 2×6 | 1 | 1.0 | 0.2 | 1.8 | 16.2 | 350 | 4.61 |
| 2×10 | 6 | 1.0 | 0.2 | 1.8 | 18.7 | 429 | 3.08 |
| 2×16 | 6 | 1.0 | 0.2 | 1.8 | 20.3 | 522 | 1.91 |
| 2×25 | 6 | 1.2 | 0.2 | 1.8 | 23.5 | 684 | 1.20 |
| 2×35 | 6 | 1.2 | 0.2 | 1.8 | 25.5 | 804 | 0.868 |
| 2×50 | 6 | 1.4 | 0.2 | 1.8 | 28.9 | 990 | 0.641 |
| 2×70 | 12 | 1.4 | 0.2 | 1.9 | 32.8 | 1261 | 0.443 |
| 2×95 | 15 | 1.6 | 0.5 | 2.1 | 38.8 | 1990 | 0.320 |
| 2×120 | 15 | 1.6 | 0.5 | 2.2 | 41.8 | 2262 | 0.253 |
| 2×150 | 15 | 1.8 | 0.5 | 2.4 | 46.4 | 2741 | 0.206 |
| 2×185 | 30 | 2.0 | 0.5 | 2.5 | 50.6 | 3221 | 0.164 |
| 2×240 | 30 | 2.2 | 0.5 | 2.7 | 56.4 | 3945 | 0.125 |
| 2×300 | 30 | 2.4 | 0.5 | 2.9 | 62.4 | 4758 | 0.100 |
| 2×400 | 53 | 2.6 | 0.5 | 3.1 | 69.2 | 5756 | 0.0778 |
| 3×2.5 | 1 | 0.8 | 0.2 | 1.8 | 14.0 | 271 | 12.1 |
| 3×4 | 1 | 1.0 | 0.2 | 1.8 | 15.8 | 343 | 7.41 |
| 3×6 | 1 | 1.0 | 0.2 | 1.8 | 16.9 | 396 | 4.61 |
| 3×10 | 6 | 1.0 | 0.2 | 1.8 | 19.7 | 491 | 3.08 |
| 3×16 | 6 | 1.0 | 0.2 | 1.8 | 21.4 | 607 | 1.91 |
| 3×25 | 6 | 1.2 | 0.2 | 1.8 | 24.8 | 808 | 1.20 |
| 3X35 | 6 | 1.2 | 0.2 | 1.8 | 27.0 | 960 | 0.868 |
| 3×50 | 6 | 1.4 | 0.2 | 1.9 | 30.9 | 1208 | 0.641 |
| 3×70 | 12 | 1.4 | 0.2 | 2.0 | 35.0 | 1555 | 0.443 |
| 3×95 | 15 | 1.6 | 0.5 | 2.2 | 41.4 | 2409 | 0.320 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×120 | 15 | 1.6 | 0.5 | 2.3 | 44.6 | 2758 | 0.253 |
| 3×150 | 15 | 1.8 | 0.5 | 2.5 | 49.5 | 3348 | 0.206 |
| 3×185 | 30 | 2.0 | 0.5 | 2.6 | 54.0 | 3963 | 0.164 |
| 3×240 | 30 | 2.2 | 0.5 | 2.8 | 60.6 | 4957 | 0.125 |
| 3×300 | 30 | 2.4 | 0.5 | 3.0 | 66.7 | 5925 | 0.100 |
| 3×400 | 53 | 2.6 | 0.5 | 3.3 | 74.6 | 7329 | 0.0778 |
| 4×2.5 | 1 | 0.8 | 0.2 | 1.8 | 14.8 | 307 | 12.1 |
| 4×4 | 1 | 1.0 | 0.2 | 1.8 | 16.9 | 394 | 7.41 |
| 4×6 | 1 | 1.0 | 0.2 | 1.8 | 18.2 | 458 | 4.61 |
| 4×10 | 6 | 1.0 | 0.2 | 1.8 | 21.2 | 573 | 3.08 |
| 4×16 | 6 | 1.0 | 0.2 | 1.8 | 23.2 | 717 | 1.91 |
| 4×25 | 6 | 1.2 | 0.2 | 1.8 | 27.0 | 965 | 1.20 |
| 4×35 | 6 | 1.2 | 0.2 | 1.9 | 29.6 | 1169 | 0.868 |
| 4×50 | 6 | 1.4 | 0.2 | 2.0 | 34.7 | 1527 | 0.641 |
| 4×70 | 12 | 1.4 | 0.5 | 2.2 | 39.9 | 2302 | 0.443 |
| 4×95 | 15 | 1.6 | 0.5 | 2.4 | 46.0 | 2987 | 0.320 |
| 4×120 | 15 | 1.6 | 0.5 | 2.5 | 49.6 | 3430 | 0.253 |
| 4×150 | 15 | 1.8 | 0.5 | 2.6 | 54.4 | 4086 | 0.206 |
| 4×185 | 30 | 2.0 | 0.5 | 2.8 | 60.0 | 4950 | 0.164 |
| 4×240 | 30 | 2.2 | 0.5 | 3.0 | 67.0 | 6129 | 0.125 |
| 4×300 | 30 | 2.4 | 0.5 | 3.2 | 74.1 | 7430 | 0.100 |
| 4×400 | 53 | 2.6 | 0.5 | 3.5 | 82.4 | 9112 | 0.0778 |
| 5×2.5 | 1 | 0.8 | 0.2 | 1.8 | 15.8 | 345 | 12.1 |
| 5×4 | 1 | 1.0 | 0.2 | 1.8 | 18.1 | 447 | 7.41 |
| 5×6 | 1 | 1.0 | 0.2 | 1.8 | 19.5 | 524 | 4.61 |
| 5×10 | 6 | 1.0 | 0.2 | 1.8 | 22.9 | 662 | 3.08 |
| 5×16 | 6 | 1.0 | 0.2 | 1.8 | 25.1 | 834 | 1.91 |
| 5×25 | 6 | 1.2 | 0.2 | 1.9 | 29.6 | 1147 | 1.20 |
| 5×35 | 6 | 1.2 | 0.2 | 1.9 | 33.0 | 1426 | 0.868 |
| 5×50 | 6 | 1.4 | 0.5 | 2.2 | 39.4 | 2202 | 0.641 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×70 | 12 | 1.4 | 0.5 | 2.3 | 43.6 | 2719 | 0.443 |
| 5×95 | 15 | 1.6 | 0.5 | 2.5 | 50.4 | 3539 | 0.320 |
| 5×120 | 15 | 1.6 | 0.5 | 2.6 | 54.3 | 4077 | 0.253 |
| 5×150 | 15 | 1.8 | 0.5 | 2.8 | 60.3 | 4963 | 0.206 |
| 5×185 | 30 | 2.0 | 0.5 | 3.0 | 66.1 | 5940 | 0.164 |
| 5×240 | 30 | 2.2 | 0.5 | 3.2 | 74.2 | 7455 | 0.125 |
| 5×300 | 30 | 2.4 | 0.5 | 3.5 | 81.8 | 8990 | 0.100 |
| 5×400 | 53 | 2.6 | 0.8 | 3.8 | 92.2 | 11931 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 16.4 | 371 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 17.9 | 442 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 20.5 | 544 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 22.7 | 680 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 26.1 | 901 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 27.9 | 1042 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 0.2 | 1.9 | 32.8 | 1373 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 0.2 | 2.1 | 36.6 | 1735 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 0.5 | 2.3 | 43.2 | 2657 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.6/1.4 | 0.5 | 2.4 | 47.2 | 3145 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.8/1.4 | 0.5 | 2.5 | 50.9 | 3633 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 0.5 | 2.7 | 56.2 | 4395 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 2.2/1.6 | 0.5 | 2.9 | 62.8 | 5449 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 2.4/1.8 | 0.5 | 3.1 | 69.1 | 6536 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 0.5 | 3.3 | 76.9 | 8039 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 17.2 | 406 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 18.9 | 493 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 21.5 | 606 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 24.2 | 764 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 27.7 | 1011 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 0.2 | 1.9 | 29.5 | 1159 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 0.2 | 2.0 | 34.9 | 1560 | 0.641/1.20 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel tape thickness | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 0.5 | 2.2 | 40.0 | 2322 | 0.443/0.868 |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 0.5 | 2.4 | 46.2 | 3000 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.6/1.4 | 0.5 | 2.5 | 50.3 | 3544 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.8/1.4 | 0.5 | 2.6 | 53.5 | 4016 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 0.5 | 2.8 | 59.9 | 4976 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 2.2/1.6 | 0.5 | 3.0 | 66.2 | 6050 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 2.4/1.8 | 0.5 | 3.2 | 72.9 | 7273 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 0.5 | 3.5 | 81.2 | 8975 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 0.2 | 1.8 | 17.7 | 426 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 0.2 | 1.8 | 19.2 | 509 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 0.2 | 1.8 | 22.2 | 634 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 0.2 | 1.8 | 24.6 | 799 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.8 | 28.5 | 1072 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 0.2 | 1.9 | 30.9 | 1268 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 0.2 | 2.1 | 36.5 | 1699 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 0.5 | 2.3 | 41.9 | 2529 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 0.5 | 2.4 | 48.2 | 3257 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.6/1.4 | 0.5 | 2.6 | 52.4 | 3821 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.8/1.4 | 0.5 | 2.7 | 57.1 | 4514 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 0.5 | 2.9 | 63.0 | 5454 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 2.2/1.6 | 0.5 | 3.1 | 70.0 | 6707 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 2.4/1.8 | 0.5 | 3.3 | 77.4 | 8145 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 0.8 | 3.7 | 87.4 | 10858 | 0.0778/0.164 |

VV72 (NYRY)  Single Core  0.6/1kV

CU/PVC/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Inner sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magneticsteel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 1.0 | 0.8 | 1.4 | 12.7 | 350 | 1.83 |
| 1×16 | 6 | 1.0 | 0.8 | 1.4 | 13.5 | 428 | 1.15 |
| 1×25 | 6 | 1.2 | 0.8 | 1.4 | 15.1 | 562 | 0.727 |
| 1×35 | 6 | 1.2 | 0.8 | 1.4 | 16.1 | 681 | 0.524 |
| 1×50 | 6 | 1.4 | 1.25 | 1.5 | 18.9 | 984 | 0.387 |
| 1×70 | 12 | 1.4 | 1.25 | 1.5 | 20.4 | 1234 | 0.268 |
| 1×95 | 15 | 1.6 | 1.25 | 1.6 | 22.8 | 1575 | 0.193 |
| 1×120 | 18 | 1.6 | 1.6 | 1.7 | 25.1 | 2004 | 0.153 |
| 1×150 | 18 | 1.8 | 1.6 | 1.7 | 27.0 | 2364 | 0.124 |
| 1×185 | 30 | 2.0 | 1.6 | 1.8 | 29.2 | 2814 | 0.0991 |
| 1×240 | 34 | 2.2 | 1.6 | 1.9 | 32.1 | 3495 | 0.0754 |
| 1×300 | 34 | 2.4 | 2.0 | 2.0 | 35.7 | 4431 | 0.0601 |
| 1×400 | 53 | 2.6 | 2.0 | 2.1 | 39.5 | 5501 | 0.0470 |
| 1×500 | 53 | 2.8 | 2.0 | 2.2 | 43.0 | 6683 | 0.0366 |
| 1×630 | 53 | 2.8 | 2.0 | 2.4 | 47.1 | 8238 | 0.0283 |

VLV72 (NAYRY)  Single Core  0.6/1kV

AL/PVC/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Aluminum,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Inner sheath: Polyvinyl chloride PVC

- Armour: Non-magnetic steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal Non-magneticsteel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 1×10 | 6 | 1.0 | 0.8 | 1.4 | 12.7 | 281 | 3.08 |
| 1×16 | 6 | 1.0 | 0.8 | 1.4 | 13.5 | 329 | 1.91 |
| 1×25 | 6 | 1.2 | 0.8 | 1.4 | 15.1 | 410 | 1.20 |
| 1×35 | 6 | 1.2 | 0.8 | 1.4 | 16.1 | 469 | 0.868 |
| 1×50 | 6 | 1.4 | 1.25 | 1.5 | 18.9 | 694 | 0.641 |
| 1×70 | 12 | 1.4 | 1.25 | 1.5 | 20.4 | 820 | 0.443 |
| 1×95 | 15 | 1.6 | 1.25 | 1.6 | 22.8 | 1001 | 0.320 |
| 1×120 | 15 | 1.6 | 1.6 | 1.7 | 25.1 | 1274 | 0.253 |
| 1×150 | 15 | 1.8 | 1.6 | 1.7 | 27.0 | 1466 | 0.206 |
| 1×185 | 30 | 2.0 | 1.6 | 1.8 | 29.2 | 1683 | 0.164 |
| 1×240 | 30 | 2.2 | 1.6 | 1.9 | 32.1 | 2028 | 0.125 |
| 1×300 | 30 | 2.4 | 2.0 | 2.0 | 35.7 | 2590 | 0.100 |
| 1×400 | 53 | 2.6 | 2.0 | 2.1 | 39.5 | 3101 | 0.0778 |
| 1×500 | 53 | 2.8 | 2.0 | 2.2 | 43.0 | 3676 | 0.0605 |
| 1×630 | 53 | 2.8 | 2.0 | 2.4 | 47.1 | 4333 | 0.0469 |

VV32 (NYRY)  Multi-Core  0.6/1kV

CU/PVC/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Copper ,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NYRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×1.5 | 1 | 0.8 | 0.8 | 1.8 | 13.7 | 322 | 12.1 |
| 2×2.5 | 1 | 0.8 | 0.8 | 1.8 | 14.5 | 367 | 7.41 |
| 2×4 | 1 | 1.0 | 0.8 | 1.8 | 16.3 | 459 | 4.61 |
| 2×6 | 1 | 1.0 | 1.25 | 1.8 | 18.2 | 652 | 3.08 |
| 2×10 | 6 | 1.0 | 1.25 | 1.8 | 20.7 | 842 | 1.83 |
| 2×16 | 6 | 1.0 | 1.25 | 1.8 | 22.3 | 1025 | 1.15 |
| 2×25 | 6 | 1.2 | 1.6 | 1.8 | 26.2 | 1501 | 0.727 |
| 2×35 | 6 | 1.2 | 1.6 | 1.8 | 28.2 | 1791 | 0.524 |
| 2×50 | 6 | 1.4 | 1.6 | 1.9 | 31.8 | 2231 | 0.387 |
| 2×70 | 12 | 1.4 | 2.0 | 2.0 | 36.5 | 3067 | 0.268 |
| 2×95 | 15 | 1.6 | 2.0 | 2.2 | 41.3 | 3907 | 0.193 |
| 2×120 | 18 | 1.6 | 2.0 | 2.3 | 44.3 | 4562 | 0.153 |
| 2×150 | 18 | 1.8 | 2.5 | 2.4 | 49.7 | 5874 | 0.124 |
| 2×185 | 30 | 2.0 | 2.5 | 2.6 | 54.1 | 6938 | 0.0991 |
| 2×240 | 34 | 2.2 | 2.5 | 2.7 | 59.7 | 8504 | 0.0754 |
| 2×300 | 34 | 2.4 | 2.5 | 2.9 | 65.7 | 10262 | 0.0601 |
| 2×400 | 53 | 2.6 | 2.5 | 3.2 | 72.7 | 12586 | 0.0470 |
| 3×1.5 | 1 | 0.8 | 0.8 | 1.8 | 14.2 | 357 | 12.1 |
| 3×2.5 | 1 | 0.8 | 0.8 | 1.8 | 15.1 | 411 | 7.41 |
| 3×4 | 1 | 1.0 | 0.8 | 1.8 | 16.9 | 528 | 4.61 |
| 3×6 | 1 | 1.0 | 1.25 | 1.8 | 18.9 | 750 | 3.08 |
| 3×10 | 6 | 1.0 | 1.25 | 1.8 | 21.7 | 991 | 1.83 |
| 3×16 | 6 | 1.0 | 1.25 | 1.8 | 23.4 | 1232 | 1.15 |
| 3×25 | 6 | 1.2 | 1.6 | 1.8 | 27.5 | 1801 | 0.727 |
| 3X35 | 6 | 1.2 | 1.6 | 1.8 | 29.7 | 2181 | 0.524 |
| 3×50 | 6 | 1.4 | 1.6 | 2.0 | 33.8 | 2777 | 0.387 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×70 | 12 | 1.4 | 2.0 | 2.1 | 38.7 | 3843 | 0.268 |
| 3×95 | 15 | 1.6 | 2.0 | 2.2 | 43.7 | 4947 | 0.193 |
| 3×120 | 18 | 1.6 | 2.0 | 2.3 | 46.9 | 5829 | 0.153 |
| 3×150 | 18 | 1.8 | 2.5 | 2.5 | 52.8 | 7454 | 0.124 |
| 3×185 | 30 | 2.0 | 2.5 | 2.7 | 57.5 | 8924 | 0.0991 |
| 3×240 | 34 | 2.2 | 2.5 | 2.9 | 64.1 | 11150 | 0.0754 |
| 3×300 | 34 | 2.4 | 2.5 | 3.1 | 70.2 | 13441 | 0.0601 |
| 3×400 | 53 | 2.6 | 3.15 | 3.4 | 79.4 | 17564 | 0.0470 |
| 4×1.5 | 1 | 0.8 | 0.8 | 1.8 | 15.0 | 398 | 12.1 |
| 4×2.5 | 1 | 0.8 | 0.8 | 1.8 | 15.9 | 468 | 7.41 |
| 4×4 | 1 | 1.0 | 1.25 | 1.8 | 18.9 | 736 | 4.61 |
| 4×6 | 1 | 1.0 | 1.25 | 1.8 | 20.2 | 869 | 3.08 |
| 4×10 | 6 | 1.0 | 1.25 | 1.8 | 23.2 | 1157 | 1.83 |
| 4×16 | 6 | 1.0 | 1.6 | 1.8 | 25.9 | 1609 | 1.15 |
| 4×25 | 6 | 1.2 | 1.6 | 1.8 | 29.7 | 2162 | 0.727 |
| 4×35 | 6 | 1.2 | 1.6 | 1.9 | 32.3 | 2669 | 0.524 |
| 4×50 | 6 | 1.4 | 2.0 | 2.1 | 38.4 | 3739 | 0.387 |
| 4×70 | 12 | 1.4 | 2.0 | 2.2 | 42.2 | 4723 | 0.268 |
| 4×95 | 15 | 1.6 | 2.5 | 2.4 | 49.3 | 6591 | 0.193 |
| 4×120 | 18 | 1.6 | 2.5 | 2.5 | 52.9 | 7775 | 0.153 |
| 4×150 | 18 | 1.8 | 2.5 | 2.7 | 57.9 | 9280 | 0.124 |
| 4×185 | 30 | 2.0 | 2.5 | 2.9 | 63.5 | 11235 | 0.0991 |
| 4×240 | 34 | 2.2 | 2.5 | 3.1 | 70.5 | 13979 | 0.0754 |
| 4×300 | 34 | 2.4 | 3.15 | 3.3 | 78.9 | 17902 | 0.0601 |
| 4×400 | 53 | 2.6 | 3.15 | 3.6 | 87.2 | 22055 | 0.0470 |
| 5×1.5 | 1 | 0.8 | 0.8 | 1.8 | 15.8 | 449 | 12.1 |
| 5×2.5 | 1 | 0.8 | 0.8 | 1.8 | 16.9 | 530 | 7.41 |
| 5×4 | 1 | 1.0 | 1.25 | 1.8 | 20.1 | 836 | 4.61 |
| 5×6 | 1 | 1.0 | 1.25 | 1.8 | 21.5 | 992 | 3.08 |
| 5×10 | 6 | 1.0 | 1.6 | 1.8 | 25.6 | 1490 | 1.83 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×16 | 6 | 1.0 | 1.6 | 1.8 | 27.8 | 1878 | 1.15 |
| 5×25 | 6 | 1.2 | 1.6 | 1.9 | 32.3 | 2563 | 0.727 |
| 5×35 | 6 | 1.2 | 2.0 | 2.0 | 36.7 | 3487 | 0.524 |
| 5×50 | 6 | 1.4 | 2.0 | 2.2 | 41.7 | 4436 | 0.387 |
| 5×70 | 12 | 1.4 | 2.0 | 2.3 | 45.9 | 5649 | 0.268 |
| 5×95 | 15 | 1.6 | 2.5 | 2.5 | 53.7 | 7849 | 0.193 |
| 5×120 | 18 | 1.6 | 2.5 | 2.7 | 57.8 | 9345 | 0.153 |
| 5×150 | 18 | 1.8 | 2.5 | 2.9 | 63.8 | 11208 | 0.124 |
| 5×185 | 30 | 2.0 | 2.5 | 3.0 | 69.4 | 13517 | 0.0991 |
| 5×240 | 34 | 2.2 | 3.15 | 3.3 | 79.0 | 17888 | 0.0754 |
| 5×300 | 34 | 2.4 | 3.15 | 3.6 | 86.6 | 21643 | 0.0601 |
| 5×400 | 53 | 2.6 | 3.15 | 3.9 | 95.8 | 26754 | 0.0470 |
| 3×2.5+1×1.5 | 1/1 | 0.8/0.8 | 0.8 | 1.8 | 15.7 | 450 | 7.41/12.1 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 18.4 | 699 | 4.61/7.41 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 19.9 | 833 | 3.08/4.61 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 1.25 | 1.8 | 22.5 | 1092 | 1.83/3.08 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 25.4 | 1527 | 1.15/1.83 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.8 | 28.8 | 2034 | 0.727/1.15 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 30.8 | 2403 | 0.524/1.15 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 2.0 | 36.5 | 3390 | 0.387/0.727 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 2.1 | 40.1 | 4261 | 0.268/0.524 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 2.0 | 2.3 | 45.5 | 5514 | 0.193/0.387 |
| 3×120+1×70 | 18/12 | 1.6/1.4 | 2.5 | 2.5 | 50.7 | 7148 | 0.153/0.268 |
| 3×150+1×70 | 18/12 | 1.8/1.4 | 2.5 | 2.6 | 54.4 | 8236 | 0.124/0.268 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 2.5 | 2.7 | 59.5 | 9994 | 0.0991/0.193 |
| 3×240+1×120 | 34/18 | 2.2/1.6 | 2.5 | 2.9 | 66.1 | 12399 | 0.0754/0.153 |
| 3×300+1×150 | 34/18 | 2.4/1.8 | 2.5 | 3.1 | 72.4 | 14964 | 0.0601/0.124 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 3.15 | 3.4 | 81.7 | 19493 | 0.0470/0.0991 |
| 3×2.5+2×1.5 | 1/1 | 0.8/0.8 | 0.8 | 1.8 | 16.4 | 496 | 7.41/12.1 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 19.2 | 762 | 4.61/7.41 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 20.9 | 931 | 3.08/4.61 |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 1.25 | 1.8 | 23.5 | 1201 | 1.83/3.08 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 26.9 | 1716 | 1.15/1.83 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 1.6 | 1.8 | 30.4 | 2280 | 0.727/1.15 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 32.2 | 2646 | 0.524/1.15 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 2.0 | 2.1 | 38.6 | 3783 | 0.387/0.727 |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 2.0 | 2.2 | 42.3 | 4751 | 0.268/0.524 |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 2.5 | 2.4 | 49.5 | 6613 | 0.193/0.387 |
| 3×120+2×70 | 18/12 | 1.6/1.4 | 2.5 | 2.5 | 53.6 | 8012 | 0.153/0.268 |
| 3×150+2×70 | 18/12 | 1.8/1.4 | 2.5 | 2.7 | 57.0 | 9114 | 0.124/0.268 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 2.5 | 2.9 | 63.4 | 11280 | 0.0991/0.193 |
| 3×240+2×120 | 34/18 | 2.2/1.6 | 2.5 | 3.0 | 69.5 | 13842 | 0.0754/0.153 |
| 3×300+2×150 | 34/18 | 2.4/1.8 | 2.5 | 3.3 | 76.4 | 16773 | 0.0601/0.124 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 3.15 | 3.6 | 86.0 | 21752 | 0.0470/0.0991 |
| 4×2.5+1×1.5 | 1/1 | 0.8/0.8 | 0.8 | 1.8 | 16.7 | 513 | 7.41/12.1 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 19.7 | 799 | 4.61/7.41 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 21.2 | 966 | 3.08/4.61 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 1.6 | 1.8 | 24.9 | 1403 | 1.83/3.08 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 27.3 | 1797 | 1.15/1.83 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 31.4 | 2420 | 0.727/1.15 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 33.6 | 2892 | 0.524/1.15 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 2.1 | 40.0 | 4086 | 0.387/0.727 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 2.3 | 44.2 | 5208 | 0.268/0.524 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 2.5 | 2.5 | 51.7 | 7261 | 0.193/0.387 |
| 4×120+1×70 | 18/12 | 1.6/1.4 | 2.5 | 2.6 | 55.7 | 8656 | 0.153/0.268 |
| 4×150+1×70 | 18/12 | 1.8/1.4 | 2.5 | 2.8 | 60.6 | 10202 | 0.124/0.268 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 2.5 | 2.9 | 66.3 | 12400 | 0.0991/0.193 |
| 4×240+1×120 | 34/18 | 2.2/1.6 | 2.5 | 3.2 | 73.5 | 15408 | 0.0754/0.153 |
| 4×300+1×150 | 34/18 | 2.4/1.8 | 3.15 | 3.4 | 82.2 | 19656 | 0.0601/0.124 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 3.15 | 3.7 | 90.8 | 24254 | 0.0470/0.0991 |

VLV32 (NAYRY)  Multi-Core  0.6/1kV

AL/PVC/SWA/PVC

APPLICATION

These power cables are used for electricity supply in low voltage installation systems. They are well adapted to underground use in industrial applications with an additional mechanical protection. They are suitable for laying Indoor, tunnel, cable trench, shaft or buried laying, The cable can withstand mechanical external forces and a certain tensile force, it widely used in transformer stations, electric power plants and industrial plants.

CONSTRUCTION

- Conductor : Aluminum,class 1 or class 2,solid or stranded, circular or circular compacted conductors

- Insulation: Polyvinyl chloride PVC

- Filler:Non-hygroscopic material

- Binder:Non-hygroscopic material

- Inner sheath: Polyvinyl chloride PVC

- Armour: Steel wire

- Binder:Non-hygroscopic material

- Outer sheath: Polyvinyl chloride PVC

MAIN CHARACTERISTICS

Good electrical and mechanical properties. Resistance to abrasion, moisture and sunlight. Adequate resistance to oil and abrasion.

SPECIFICATION

IEC 60228 Conductors of insulate cables

IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from         1 kV(Um=1.2kV) up to 30kV(Um=36kV) - Part 1:Cables for rated voltages of 1 kV (Um=1.2kV) and       3 kV(Um=3.6kV)

POWER CABLE NAYRY

IEC 60502-1

| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 2×2.5 | 1 | 0.8 | 0.8 | 1.8 | 14.5 | 338 | 12.1 |
| 2×4 | 1 | 1.0 | 0.8 | 1.8 | 16.3 | 415 | 7.41 |
| 2×6 | 1 | 1.0 | 1.25 | 1.8 | 18.2 | 592 | 4.61 |
| 2×10 | 6 | 1.0 | 1.25 | 1.8 | 20.7 | 697 | 3.08 |
| 2×16 | 6 | 1.0 | 1.25 | 1.8 | 22.3 | 827 | 1.91 |
| 2×25 | 6 | 1.2 | 1.6 | 1.8 | 26.2 | 1194 | 1.20 |
| 2×35 | 6 | 1.2 | 1.6 | 1.8 | 28.2 | 1366 | 0.868 |
| 2×50 | 6 | 1.4 | 1.6 | 1.9 | 31.8 | 1627 | 0.641 |
| 2×70 | 12 | 1.4 | 2.0 | 2.0 | 36.5 | 2235 | 0.443 |
| 2×95 | 15 | 1.6 | 2.0 | 2.2 | 41.3 | 2753 | 0.320 |
| 2×120 | 15 | 1.6 | 2.0 | 2.3 | 44.3 | 3088 | 0.253 |
| 2×150 | 15 | 1.8 | 2.5 | 2.4 | 49.7 | 4070 | 0.206 |
| 2×185 | 30 | 2.0 | 2.5 | 2.6 | 54.1 | 4666 | 0.164 |
| 2×240 | 30 | 2.2 | 2.5 | 2.7 | 59.7 | 5555 | 0.125 |
| 2×300 | 30 | 2.4 | 2.5 | 2.9 | 65.7 | 6556 | 0.100 |
| 2×400 | 53 | 2.6 | 2.5 | 3.2 | 72.7 | 7762 | 0.0778 |
| 3×2.5 | 1 | 0.8 | 0.8 | 1.8 | 15.1 | 368 | 12.1 |
| 3×4 | 1 | 1.0 | 0.8 | 1.8 | 16.9 | 456 | 7.41 |
| 3×6 | 1 | 1.0 | 1.25 | 1.8 | 18.9 | 643 | 4.61 |
| 3×10 | 6 | 1.0 | 1.25 | 1.8 | 21.7 | 783 | 3.08 |
| 3×16 | 6 | 1.0 | 1.25 | 1.8 | 23.4 | 934 | 1.91 |
| 3×25 | 6 | 1.2 | 1.6 | 1.8 | 27.5 | 1341 | 1.20 |
| 3X35 | 6 | 1.2 | 1.6 | 1.8 | 29.7 | 1544 | 0.868 |
| 3×50 | 6 | 1.4 | 1.6 | 2.0 | 33.8 | 1900 | 0.641 |
| 3×70 | 12 | 1.4 | 2.0 | 2.1 | 38.7 | 2595 | 0.443 |
| 3×95 | 15 | 1.6 | 2.0 | 2.2 | 43.7 | 3216 | 0.320 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×120 | 15 | 1.6 | 2.0 | 2.3 | 46.9 | 3624 | 0.253 |
| 3×150 | 15 | 1.8 | 2.5 | 2.5 | 52.8 | 4749 | 0.206 |
| 3×185 | 30 | 2.0 | 2.5 | 2.7 | 57.5 | 5515 | 0.164 |
| 3×240 | 30 | 2.2 | 2.5 | 2.9 | 64.1 | 6727 | 0.125 |
| 3×300 | 30 | 2.4 | 2.5 | 3.1 | 70.2 | 7846 | 0.100 |
| 3×400 | 53 | 2.6 | 3.15 | 3.4 | 79.4 | 10396 | 0.0778 |
| 4×2.5 | 1 | 0.8 | 0.8 | 1.8 | 15.9 | 410 | 12.1 |
| 4×4 | 1 | 1.0 | 1.25 | 1.8 | 18.9 | 641 | 7.41 |
| 4×6 | 1 | 1.0 | 1.25 | 1.8 | 20.2 | 726 | 4.61 |
| 4×10 | 6 | 1.0 | 1.25 | 1.8 | 23.2 | 885 | 3.08 |
| 4×16 | 6 | 1.0 | 1.6 | 1.8 | 25.9 | 1213 | 1.91 |
| 4×25 | 6 | 1.2 | 1.6 | 1.8 | 29.7 | 1549 | 1.20 |
| 4×35 | 6 | 1.2 | 1.6 | 1.9 | 32.3 | 1819 | 0.868 |
| 4×50 | 6 | 1.4 | 2.0 | 2.1 | 38.4 | 2546 | 0.641 |
| 4×70 | 12 | 1.4 | 2.0 | 2.2 | 42.2 | 3058 | 0.443 |
| 4×95 | 15 | 1.6 | 2.5 | 2.4 | 49.3 | 4283 | 0.320 |
| 4×120 | 15 | 1.6 | 2.5 | 2.5 | 52.9 | 4837 | 0.253 |
| 4×150 | 15 | 1.8 | 2.5 | 2.7 | 57.9 | 5672 | 0.206 |
| 4×185 | 30 | 2.0 | 2.5 | 2.9 | 63.5 | 6690 | 0.164 |
| 4×240 | 30 | 2.2 | 2.5 | 3.1 | 70.5 | 8082 | 0.125 |
| 4×300 | 30 | 2.4 | 3.15 | 3.3 | 78.9 | 10497 | 0.100 |
| 4×400 | 53 | 2.6 | 3.15 | 3.6 | 87.2 | 12502 | 0.0778 |
| 5×2.5 | 1 | 0.8 | 0.8 | 1.8 | 16.9 | 458 | 12.1 |
| 5×4 | 1 | 1.0 | 1.25 | 1.8 | 20.1 | 717 | 7.41 |
| 5×6 | 1 | 1.0 | 1.25 | 1.8 | 21.5 | 823 | 4.61 |
| 5×10 | 6 | 1.0 | 1.6 | 1.8 | 25.6 | 1147 | 3.08 |
| 5×16 | 6 | 1.0 | 1.6 | 1.8 | 27.8 | 1382 | 1.91 |
| 5×25 | 6 | 1.2 | 1.6 | 1.9 | 32.3 | 1798 | 1.20 |
| 5×35 | 6 | 1.2 | 2.0 | 2.0 | 36.7 | 2424 | 0.868 |
| 5×50 | 6 | 1.4 | 2.0 | 2.2 | 41.7 | 2951 | 0.641 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 5×70 | 12 | 1.4 | 2.0 | 2.3 | 45.9 | 3569 | 0.443 |
| 5×95 | 15 | 1.6 | 2.5 | 2.5 | 53.7 | 4964 | 0.320 |
| 5×120 | 15 | 1.6 | 2.5 | 2.7 | 57.8 | 5633 | 0.253 |
| 5×150 | 15 | 1.8 | 2.5 | 2.9 | 63.8 | 6699 | 0.206 |
| 5×185 | 30 | 2.0 | 2.5 | 3.0 | 69.4 | 7837 | 0.164 |
| 5×240 | 30 | 2.2 | 3.15 | 3.3 | 79.0 | 10517 | 0.125 |
| 5×300 | 30 | 2.4 | 3.15 | 3.6 | 86.6 | 12324 | 0.100 |
| 5×400 | 53 | 2.6 | 3.15 | 3.9 | 95.8 | 14750 | 0.0778 |
| 3×4+1×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 18.4 | 612 | 7.41/12.1 |
| 3×6+1×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 19.9 | 712 | 4.61/7.41 |
| 3×10+1×6 | 6/1 | 1.0/1.0 | 1.25 | 1.8 | 22.5 | 850 | 3.08/4.61 |
| 3×16+1×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 25.4 | 1164 | 1.91/3.08 |
| 3×25+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.8 | 28.8 | 1476 | 1.20/1.91 |
| 3×35+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 30.8 | 1667 | 0.868/1.91 |
| 3×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 2.0 | 36.5 | 2326 | 0.641/1.20 |
| 3×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 2.1 | 40.1 | 2801 | 0.443/0.868 |
| 3×95+1×50 | 15/6 | 1.6/1.4 | 2.0 | 2.3 | 45.5 | 3491 | 0.320/0.641 |
| 3×120+1×70 | 15/12 | 1.6/1.4 | 2.5 | 2.5 | 50.7 | 4489 | 0.253/0.443 |
| 3×150+1×70 | 15/12 | 1.8/1.4 | 2.5 | 2.6 | 54.4 | 5114 | 0.206/0.443 |
| 3×185+1×95 | 30/15 | 2.0/1.6 | 2.5 | 2.7 | 59.5 | 6008 | 0.164/0.320 |
| 3×240+1×120 | 30/15 | 2.2/1.6 | 2.5 | 2.9 | 66.1 | 7240 | 0.125/0.253 |
| 3×300+1×150 | 30/15 | 2.4/1.8 | 2.5 | 3.1 | 72.4 | 8509 | 0.100/0.206 |
| 3×400+1×185 | 53/30 | 2.6/2.0 | 3.15 | 3.4 | 81.7 | 11193 | 0.0778/0.164 |
| 3×4+2×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 19.2 | 661 | 7.41/12.1 |
| 3×6+2×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 20.9 | 776 | 4.61/7.41 |
| 3×10+2×6 | 6/1 | 1.0/1.0 | 1.25 | 1.8 | 23.5 | 934 | 3.08/4.61 |
| 3×16+2×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 26.9 | 1287 | 1.91/3.08 |
| 3×25+2×16 | 6/6 | 1.2/1.0 | 1.6 | 1.8 | 30.4 | 1624 | 1.20/1.91 |
| 3×35+2×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 32.2 | 1811 | 0.868/1.91 |
| 3×50+2×25 | 6/6 | 1.4/1.2 | 2.0 | 2.1 | 38.6 | 2603 | 0.641/1.20 |
| No. of cores and nominal cross section | Min. Number of wires | Nominal insulation thickness | Nominal steel wire diameter | Nominal sheath thickness | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor at 20℃ |
| No.× mm2 | No. | mm | mm | mm | mm | kg/km | Ω/km |
| 3×70+2×35 | 12/6 | 1.4/1.2 | 2.0 | 2.2 | 42.3 | 3077 | 0.443/0.868 |
| 3×95+2×50 | 15/6 | 1.6/1.4 | 2.5 | 2.4 | 49.5 | 4298 | 0.320/0.641 |
| 3×120+2×70 | 15/12 | 1.6/1.4 | 2.5 | 2.5 | 53.6 | 4977 | 0.253/0.443 |
| 3×150+2×70 | 15/12 | 1.8/1.4 | 2.5 | 2.7 | 57.0 | 5576 | 0.206/0.443 |
| 3×185+2×95 | 30/15 | 2.0/1.6 | 2.5 | 2.9 | 63.4 | 6717 | 0.164/0.320 |
| 3×240+2×120 | 30/15 | 2.2/1.6 | 2.5 | 3.0 | 69.5 | 7948 | 0.125/0.253 |
| 3×300+2×150 | 30/15 | 2.4/1.8 | 2.5 | 3.3 | 76.4 | 9417 | 0.100/0.206 |
| 3×400+2×185 | 53/30 | 2.6/2.0 | 3.15 | 3.6 | 86.0 | 12318 | 0.0778/0.164 |
| 4×4+1×2.5 | 1/1 | 1.0/0.8 | 1.25 | 1.8 | 19.7 | 689 | 7.41/12.1 |
| 4×6+1×4 | 1/1 | 1.0/1.0 | 1.25 | 1.8 | 21.2 | 799 | 4.61/7.41 |
| 4×10+1×6 | 6/1 | 1.0/1.0 | 1.6 | 1.8 | 24.9 | 1106 | 3.08/4.61 |
| 4×16+1×10 | 6/6 | 1.0/1.0 | 1.6 | 1.8 | 27.3 | 1335 | 1.91/3.08 |
| 4×25+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 31.4 | 1709 | 1.20/1.91 |
| 4×35+1×16 | 6/6 | 1.2/1.0 | 1.6 | 1.9 | 33.6 | 1943 | 0.868/1.91 |
| 4×50+1×25 | 6/6 | 1.4/1.2 | 2.0 | 2.1 | 40.0 | 2767 | 0.641/1.20 |
| 4×70+1×35 | 12/6 | 1.4/1.2 | 2.0 | 2.3 | 44.2 | 3331 | 0.443/0.868 |
| 4×95+1×50 | 15/6 | 1.6/1.4 | 2.5 | 2.5 | 51.7 | 4660 | 0.320/0.641 |
| 4×120+1×70 | 15/12 | 1.6/1.4 | 2.5 | 2.6 | 55.7 | 5303 | 0.253/0.443 |
| 4×150+1×70 | 15/12 | 1.8/1.4 | 2.5 | 2.8 | 60.6 | 6178 | 0.206/0.443 |
| 4×185+1×95 | 30/15 | 2.0/1.6 | 2.5 | 2.9 | 66.3 | 7279 | 0.164/0.320 |
| 4×240+1×120 | 30/15 | 2.2/1.6 | 2.5 | 3.2 | 73.5 | 8735 | 0.125/0.253 |
| 4×300+1×150 | 30/15 | 2.4/1.8 | 3.15 | 3.4 | 82.2 | 11350 | 0.100/0.206 |
| 4×400+1×185 | 53/30 | 2.6/2.0 | 3.15 | 3.7 | 90.8 | 13504 | 0.0778/0.164 |

Current Rating (in accordance with IEC 60287)

The current rating is calculated according to the following conditions. One multi-core cables or one three phase group of single-core cables.

Maximum conductor temperature: 70℃

Temperature of the ground : 25℃

Temperature of ambient air : 40℃

Laying depth : 0.7m

Thermal resistivity of the ground : 1.0 K·m/W

Spacing between cable laid: In flat formation 2 times of cable overall diameter,

In trefoil with cable touching.

Where the site conditions differ from the standard conditions mentioned, it will be necessary to multiply the tabulated ratings by the actors given in the following tables. These factors are for variation in ambient air temperature,in ambient ground temperature and soil thermal resistivity.

Rating Factors

Cables laid direct in air:

Correction factors for ambient air temperatures other than 40 °C.

| Maximum conductor temperature °C | Ambient air temperature °C |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 |
| 70 | 1.29 | 1.22 | 1.15 | 1.08 | 1.00 | 0.91 | 0.81 | 0.71 |

Cables laid direct in ground:

Correction factors for ambient ground temperatures other than 25 °C.

| Maximum conductor temperature °C | Ambient ground temperature °C |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 10 | 15 | 20 | 25 | 30 | 35 |
| 70 | 1.15 | 1.11 | 1.05 | 1.00 | 0.94 | 0.88 |

The correction factors of current capacity for different soil thermal resistivity.

| Values of soil thermal resistivity K· m/W | 0.8 | 1.0 | 1.2 | 1.5 |
| --- | --- | --- | --- | --- |
| The Correction Factors of Current Capacity | 1.08 | 1.00 | 0.95 | 0.77 |

Current ratings for single-core cables

| Arrangement | Trefoil |  |  |  | Flat spaced |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 19 | -- | 27 | -- | 24 | -- | 29 | -- |
| 2.5 | 24 | 19 | 36 | 27 | 31 | 24 | 38 | 30 |
| 4 | 32 | 25 | 47 | 35 | 41 | 32 | 49 | 39 |
| 6 | 40 | 33 | 58 | 46 | 52 | 43 | 61 | 50 |
| 10 | 55 | 42 | 81 | 62 | 70 | 55 | 84 | 65 |
| 16 | 74 | 58 | 105 | 82 | 97 | 75 | 110 | 85 |
| 25 | 95 | 74 | 130 | 100 | 120 | 96 | 135 | 105 |
| 35 | 115 | 90 | 160 | 120 | 150 | 115 | 165 | 125 |
| 50 | 140 | 110 | 185 | 145 | 180 | 140 | 195 | 150 |
| 70 | 180 | 140 | 230 | 180 | 230 | 180 | 240 | 185 |
| 95 | 220 | 170 | 275 | 215 | 280 | 215 | 290 | 225 |
| 120 | 255 | 200 | 315 | 245 | 325 | 255 | 325 | 255 |
| 150 | 295 | 230 | 350 | 275 | 375 | 290 | 370 | 285 |
| 185 | 340 | 265 | 395 | 310 | 430 | 335 | 420 | 325 |
| 240 | 405 | 320 | 460 | 360 | 515 | 400 | 485 | 380 |
| 300 | 470 | 370 | 515 | 405 | 595 | 465 | 550 | 430 |
| 400 | 550 | 435 | 585 | 465 | 700 | 550 | 630 | 490 |
| 500 | 635 | 510 | 655 | 530 | 810 | 640 | 715 | 565 |
| 630 | 735 | 600 | 740 | 605 | 950 | 760 | 820 | 655 |

Current ratings for multi-core unarmoured cables

| Arrangement | Two-core |  |  |  | Three-core and above |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 19 | -- | 26 | -- | 17 | -- | 22 | -- |
| 2.5 | 25 | 19 | 34 | 26 | 21 | 17 | 29 | 23 |
| 4 | 33 | 26 | 44 | 35 | 28 | 22 | 38 | 30 |
| 6 | 42 | 34 | 56 | 45 | 36 | 29 | 47 | 39 |
| 10 | 58 | 44 | 84 | 59 | 49 | 38 | 72 | 50 |
| 16 | 76 | 59 | 110 | 85 | 66 | 51 | 94 | 73 |
| 25 | 98 | 76 | 140 | 110 | 84 | 65 | 120 | 94 |
| 35 | 120 | 93 | 175 | 135 | 100 | 80 | 145 | 110 |
| 50 | 145 | 115 | 205 | 160 | 125 | 98 | 175 | 135 |
| 70 | 185 | 145 | 255 | 195 | 160 | 120 | 210 | 165 |
| 95 | 230 | 170 | 305 | 235 | 195 | 150 | 255 | 200 |
| 120 | 265 | 205 | 350 | 270 | 235 | 180 | 295 | 230 |
| 150 | 305 | 235 | 390 | 305 | 260 | 200 | 330 | 255 |
| 185 | 350 | 275 | 440 | 345 | 305 | 235 | 370 | 290 |
| 240 | -- | -- | -- | -- | 360 | 280 | 425 | 335 |
| 300 | -- | -- | -- | -- | 410 | 320 | 480 | 375 |
| 400 | -- | -- | -- | -- | 485 | 380 | 555 | 435 |

Current ratings for multi-core armoured cables

| Arrangement | Two-core |  |  |  | Three-core and above |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Laying | In Air |  | In the ground |  | In Air |  | In the ground |  |
| Cross-section | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| mm2 | Current rating (A) |  |  |  |  |  |  |  |
| 1.5 | 17 | -- | 26 | -- | 15 | -- | 22 | -- |
| 2.5 | 23 | 18 | 34 | 26 | 19 | 15 | 29 | 23 |
| 4 | 31 | 24 | 44 | 35 | 26 | 20 | 38 | 30 |
| 6 | 38 | 32 | 56 | 45 | 32 | 26 | 47 | 39 |
| 10 | 53 | 42 | 76 | 59 | 50 | 35 | 70 | 50 |
| 16 | 71 | 55 | 100 | 77 | 66 | 51 | 92 | 71 |
| 25 | 90 | 70 | 125 | 100 | 85 | 66 | 115 | 92 |
| 35 | 110 | 86 | 175 | 120 | 105 | 81 | 140 | 110 |
| 50 | 135 | 105 | 205 | 145 | 125 | 98 | 175 | 130 |
| 70 | 185 | 130 | 255 | 195 | 160 | 120 | 205 | 160 |
| 95 | 230 | 165 | 305 | 235 | 195 | 150 | 250 | 195 |
| 120 | 265 | 190 | 350 | 270 | 235 | 180 | 290 | 225 |
| 150 | 305 | 235 | 390 | 305 | 265 | 205 | 325 | 250 |
| 185 | 350 | 275 | 440 | 345 | 300 | 235 | 365 | 285 |
| 240 | -- | -- | -- | -- | 355 | 280 | 420 | 330 |
| 300 | -- | -- | -- | -- | 410 | 320 | 475 | 370 |
| 400 | -- | -- | -- | -- | 480 | 380 | 540 | 430 |

Short Circuit Current

Short circuit current of PVC insulated cable conductor is calculated according to IEC 60949, IEC 60724. Initial temperature is 70˚C,final temperature shall not exceed160˚C when the cables conductor section not exceed300sq.mm, not exceed 140˚C when the cables conductor section more than 300sq.mm.

| Nominal area of conductor | Short circuit current (kA). Time |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Copper conductors |  |  | Aluminum conductors |  |  |
| mm2 | 1sec | 2sec | 3sec | 1sec | 2sec | 3sec |
| 1.5 | 0.17 | 0.12 | 0.10 | 0.11 | 0.08 | 0.07 |
| 2.5 | 0.29 | 0.20 | 0.17 | 0.19 | 0.13 | 0.11 |
| 4 | 0.46 | 0.33 | 0.27 | 0.30 | 0.22 | 0.18 |
| 6 | 0.69 | 0.49 | 0.40 | 0.46 | 0.32 | 0.26 |
| 10 | 1.15 | 0.81 | 0.66 | 0.76 | 0.54 | 0.44 |
| 16 | 1.84 | 1.30 | 1.06 | 1.22 | 0.86 | 0.70 |
| 25 | 2.9 | 2.0 | 1.7 | 1.9 | 1.3 | 1.1 |
| 35 | 4.0 | 2.8 | 2.3 | 2.7 | 1.9 | 1.5 |
| 50 | 5.8 | 4.1 | 3.3 | 3.8 | 2.7 | 2.2 |
| 70 | 8.1 | 5.7 | 4.6 | 5.3 | 3.8 | 3.1 |
| 95 | 10.9 | 7.7 | 6.3 | 7.2 | 5.1 | 4.2 |
| 120 | 13.8 | 9.8 | 8.0 | 9.1 | 6.5 | 5.3 |
| 150 | 17.3 | 12.2 | 10.0 | 11.4 | 8.1 | 6.6 |
| 185 | 21.3 | 15.0 | 12.3 | 14.1 | 9.9 | 8.1 |
| 240 | 27.6 | 19.5 | 15.9 | 18.2 | 12.9 | 10.5 |
| 300 | 34.5 | 24.4 | 19.9 | 22.8 | 16.1 | 13.2 |
| 400 | 41.1 | 29.1 | 23.7 | 27.2 | 19.2 | 15.7 |
| 500 | 51.4 | 36.3 | 29.7 | 34.0 | 24.0 | 19.6 |
| 630 | 64.8 | 45.8 | 37.4 | 42.8 | 30.3 | 24.7 |

编制：轩娜红/李淋淋   标准化：彭信蕊      初审：肖楠楠        审核：杨坤坤      批准：